May 7, 2020	                                     				Agenda ID #18406

TO:  	STAKEHOLDERS TO LIBERTY UTILITIES (CALPECO ELECTRIC) 2020 WILDFIRE MITIGATION PLAN Service List(s): R.18-10-007

Enclosed is the Action Statement of the Wildfire Safety Division (WSD) and Draft Resolution WSD-007.  The Action Statement and Draft Resolution WSD-007, together with the Draft Guidance Resolution WSD-002, present the WSD’s evaluation of Liberty Utilities’ 2020 Wildfire Mitigation Plan (WMP).  Pursuant to Public Utilities Code Section 8386.3(a), the attached Action Statement, the discussion found in Draft Resolution WSD-007, and the overarching discussion in Draft Guidance Resolution WSD-002 is the outcome of WSD’s review of Liberty Utilities’ WMP, including input from the public, the Wildfire Safety Advisory Board, and other governmental agencies.  The Action Statement is the conditional approval of Liberty Utilities’ WMP and is presented to the Commission for ratification via the associated resolution.

Draft Resolution WSD-007 is one of seven Draft Resolutions, sequentially ordered as Draft Resolutions WSD-003 – WSD-009, that address the individual 2020 WMPs of Pacific Gas and Electric Company, Southern California Edison Company, San Diego Gas and Electric Company, Liberty Utilities, PacifiCorp, Bear Valley Electric Service, and, together, Trans Bay Cable, LLC, and Horizon West Transmission, LLC. These seven resolutions, along with the associated Action Statements and the Draft Guidance Resolution (WSD-002), represent the totality of WSD’s evaluation of the 2020 WMPs.

Pursuant to Rule 14.5 of the Commission’s Rules of Practice and Procedure, stakeholders may submit comments on the Draft Resolutions and the Draft Guidance Resolution WSD-002 - WSD-009.  The WSD will accept one set of comments per stakeholder that collectively addresses the Draft Guidance Resolution and the individual electrical corporation Draft Resolutions 
WSD-002 - WSD-009.

Comments shall be limited to twenty (20) pages in length and should list the recommended changes to the Draft Resolutions.  Comments shall focus on factual, legal or technical errors in the proposed Draft Resolutions.

Comments must be received by the Wildfire Safety Division by May 27, 2020.  Comments should be submitted to the following email address: wildfiresafetydivision@cpuc.ca.gov. The WSD will consider comments on the Draft Resolutions when finalizing its Action Statement on Liberty Utilities’ 2020 WMP.

Stakeholders submitting comments on the Draft Resolution must also serve their comments on the service list of R.18-10-007.  Comments that are not served on the service list of R.18-10-007 may not be considered.  The WSD will post all comments received on the following website: www.cpuc.ca.gov/wildfiremitigationplans.

Replies to comments will not be accepted nor considered if submitted.

Draft Resolution WSD-007 will appear on the agenda at the next Commission meeting, which is at least 30 days after the date of this letter.  The Commission may vote to ratify WSD’s Draft Resolution at that time or it may postpone a vote until a later meeting.

Sincerely,

/s/  CAROLINE THOMAS JACOBS

Caroline Thomas Jacobs

Director, Wildfire Safety Division

California Public Utilities Commission

CTJ:mph

Attachment

May 7, 2020

Wildfire Safety Division Draft Action Statement on

Liberty Utilities/CalPeco Electric’s 2020 Wildfire Mitigation Plan

This Action Statement is the conditional approval of Liberty Utilities/CalPeco Electric’s (Liberty) Wildfire Mitigation Plan (WMP) and is presented to the California Public Utilities Commission (CPUC) for ratification, via the associated Resolution and Guidance Resolution.

Introduction

Wildfires have caused significant social, economic, and environmental damage on a global scale. In California, electric utilities are responsible for some of the most devastating wildfires in recent years. The Wildfire Safety Division (WSD) recognizes that the wildfire threat is only increasing, with utility-related ignitions responsible for a disproportionate share of wildfire-related consequences. To that end, the WSD has a vision of moving towards a sustainable California, with no catastrophic utility-related wildfires, that has access to safe, affordable, and reliable electricity. The WSD recognizes it is critical for utilities to act quickly to reduce utility-related wildfire risk effectively and prudently.

As utility wildfire mitigation has become an increasingly urgent priority, the California Legislature has passed several bills related to utility wildfire prevention and oversight. The main regulatory vehicle for the WSD to regulate utilities in reducing utility wildfire risk is the Wildfire Mitigation Plan (WMP), which was introduced in Senate Bill (SB) 1028 (Hill, 2016) and further defined in SB 901 (Dodd, 2018), Assembly Bill (AB) 1054 (Holden, 2019), and AB 111 (Committee on Budget, 2019). Investor-owned electric utilities are required to submit WMPs assessing their level of wildfire risk and providing plans for wildfire risk reduction. The first WMPs under the SB 901 framework were submitted by the utilities and evaluated by the CPUC in 2019.

AB 1054 and AB 111 transferred responsibility for evaluation and approval of WMPs to the WSD, which, as of July 2021, will transfer and become the Office of Energy Infrastructure Safety within the California Natural Resources Agency. In this role, the WSD must ensure utility wildfire mitigation efforts sufficiently address increasing utility wildfire risk. To support its efforts, the WSD is developing a draft long-term strategy and roadmap. This strategy and roadmap will inform the WSD’s work in updating the WMP process and guidelines, and the WSD’s evaluation of the WMPs.

AB 1054 mandates that the WSD complete its evaluation of WMPs within 90 days of submission. The utilities submitted 2020 WMPs on February 7, 2020. Upon completion of the past 90 days of evaluation, the WSD recognizes that the utilities have made significant progress. Compared to their first submissions in 2019, the utilities utilize much more data and objective content in their 2020 WMP filings and share more critical information with key partners. However, while utilities are already undertaking wildfire mitigation activities and building capabilities subject to regulation, all utilities must continue to make meaningful progress. Utilities’ activities need to incorporate longer-term thinking by focusing more systematically on increasing their maturity over time. All utilities should take a more robust strategic approach that leverages additional Risk Spend Efficiency (RSE) data to focus on the most impactful actions – all with a local lens. This statement outlines more specifically what the WSD sees as critical priorities for the upcoming year for Liberty and approves, with conditions, Liberty’s 2020 WMP. Together, this statement, the associated Resolution and the Guidance Resolution represent the totality of the WSD’s conditional approval of Liberty’s 2020 WMP.

Background

To ensure that utility wildfire mitigation efforts sufficiently address increasing utility wildfire risk, new WMP Guidelines, a Utility Survey and a Maturity Model were launched for 2020. Together, these tools represent a milestone in the evolution of utilities’ wildfire mitigation efforts and ensure consistency with the WSD’s enabling legislation.

2020 Guidelines

The 2020 WMP Guidelines implement several changes to further enhance the depth, comparability and quality of utility WMP submissions. Specifically, the WMP Guidelines require reporting of consistent metrics, ignitions, risk data and specific utility initiatives to reduce wildfire risk. Utilities have provided historical metrics and data as a baseline, which can be used to evaluate a utility’s wildfire risk level and to assess whether the utility’s initiatives sufficiently address this risk. These metrics and data will be used to track utility progress in mitigating the risk of catastrophic wildfire over time.

Maturity Model and Utility Survey

In order to enhance the focus on safety, ensure consistent goals and evaluate performance, the WSD has developed a model for evaluating current and projected wildfire risk reduction performance. It is important to note that this model is not designed to immediately penalize utilities for poor performance, but rather it is an effort by the WSD to work collectively with the utilities it regulates to facilitate improvement by identifying best practices, current strengths and current weaknesses across the utility landscape. The WSD believes it is in the best interest of the utilities, ratepayers and other key stakeholders to take this collaborative, growth-oriented approach. While certain utilities are currently on the low end of the range for various categories of performance, the WSD is hopeful that providing clear review and evaluation of performance, including identifying such weaknesses, will help drive change in the utilities, allowing all regulated electric utilities in California to improve wildfire risk reduction performance.

As a consequence, the model results are best interpreted as levels – the results are not absolute scores. A utility, for example, could be on the borderline for level 2 in the model, but it would remain at level 1 until it completed 100% of the steps required to cross the threshold to level 2. In this example, the way the model works is the utility would get a result of 1, not 1.8. The purpose of the model is not to penalize the utility for achieving a result of 1 but to identify the specific actions it can take to reach level 2.

Summary of the WSD’s Assessment

An effective WMP should have three, overarching components in which utilities should be striving to be “world class.” First, the WMP should demonstrate an understanding of a utility’s unique risk. Each utility should measure outcome and progress metrics and use a sophisticated model to lay the foundation for safe operation within its service territory. Second, with a deep understanding of its risk, the utility should deploy a suite of initiatives designed to incrementally and aggressively reduce that risk. Finally, this deployment should be done with a key, strategic eye toward maximizing every scarce resource, whether it be direct costs, personnel, or time, to maximize its impact. The result should be that with each passing year California is safer from wildfire threats, with a significant reduction and eventual elimination of the need to use Public Safety Power Shutoffs (PSPS) as a mitigation action.

The WSD evaluated 2020 WMPs considering the following factors:

- Completeness: The WMP is complete and comprehensively responds to the WMP requirements

- Technical feasibility and effectiveness: Initiatives proposed in the WMP are technically feasible and are effective in addressing the risks that exist in the utility’s territory

- Resource use efficiency: Initiatives are an efficient use of utility resources

- Forward looking growth: The utility is targeting maturity growth

The WSD used the utilities’ 2020 WMP submissions and subsequent updates, public comments, responses to the WSD’s data requests, utility reported data and utility responses to the Utility Survey in its assessment of 2020 WMPs.

Upon completion of this review, the WSD then determined whether each utility’s 2020 WMP should either be:

- Approved without conditions (Full Approval)

- Approved with conditions (Conditional Approval)

- Denied (Denial)

Pursuant to Public Utilities Code Section 8386.3(a), this Action Statement and the discussion found in the associated Resolutions is the outcome of the WSD’s review of Liberty’s WMP and input from the public and other governmental agencies. As stated previously, this Action Statement is the conditional approval of Liberty’s WMP and is presented to the CPUC for ratification, via the associated Resolution and Guidance Resolution.

The conditions for approval of Liberty’s WMP are designed to address the gaps identified in Liberty’s WMP. Some of the key deficiencies for Liberty’s WMP are summarized below. The associated Resolution and Guidance Resolution capture the WSD’s comprehensive review of Liberty’s WMP submission.

Discussion of WMP Assessment

Summary

Liberty primarily serves customers in the Lake Tahoe Basin with significant portions of its grid in High Fire-Threat District (HFTD) areas. For Liberty’s plan to be effective with its limited resources compared to larger utilities, strategic prioritization of initiatives by ignition driver to target the highest risk elements of Liberty’s grid is crucial.

Liberty does not currently have the tools or models necessary for risk mapping, though the utility stated that it is in the process of developing a tool that would show ignition probability by circuit. Liberty outlines various wildfire mitigation programs that address the major risk drivers in its territory, however, its vegetation management and asset management programs are focused on meeting compliance requirements and are not risk-based.

Liberty also does not provide a detailed justification of how it determined its portfolio of planned initiatives to be the most effective use of its resources. Liberty, like peer small and multijurisdictional utilities (SMJUs), has not been subject to Safety Model Assessment Proceedings (S-MAP) or Risk Assessment Mitigation Phase (RAMP) requirements and is thus just beginning the process of risk-informed decision making when it comes to wildfire mitigation activities.

Finally, based on the WSD’s assessment of Liberty’s responses to the Utility Survey against the Utility Wildfire Mitigation Maturity Model, compared to its peer utilities, Liberty is on the lower end for maturity of its capabilities. Liberty has high projected maturity growth for data governance capabilities. Liberty, however, does not fully describe how this growth will be achieved in its WMP.

Risk Assessment

Liberty’s initiatives are targeted to major risk drivers at a high level, but Liberty could do more to prioritize wildfire risk reduction. Given the growing wildfire risk brought on by climate change, all utilities must move away from traditional prioritization practices to those informed and prioritized by risk. Liberty must rigorously apply a risk-based prioritization lens to its portfolio of initiatives to reduce wildfire risk and minimize PSPS incidents.

Liberty does not have the foundational risk assessment and data governance capabilities needed to understand its risk profile at the level of granularity necessary to inform a risk-ranked wildfire mitigation strategy. Liberty claims that its planned ignition probability tool would show ignition probability by circuit, which will be a meaningful step forward in maturing this capability. Liberty should continue to push itself to develop risk assessment and mapping and situational awareness and forecasting capabilities.

Liberty does not describe in granular detail where asset remediation, vegetation management, and grid hardening initiatives are most necessary, nor how it prioritizes deployment of those initiatives. Liberty’s WMP proposes to maintain a three-year cycle of vegetation inspections, except for Tier 3 High Fire Threat District areas, which is inadequate to meet increasing wildfire risks.

Initiatives

In general, Liberty’s initiatives, which are the actions and programs Liberty will take to reduce wildfire risk, address Liberty’s major risk factors. In its metrics reporting in its WMP, Liberty reported one ignition each due to vegetation contact, additional object contact, conductor failure, additional equipment failure, and other. The utility plans to spend 51% of its proposed spending on grid design and system hardening, 31% on vegetation management (a greater share than peers) and 13% on asset management and inspections.

Liberty reported one use of PSPS over the last five years, for a total of ninety customer hours. Normalized per Red Flag Warning circuit mile day, Liberty’s rate of PSPS use is at the low end of all utilities. The WSD found that the utility has an inadequate process for inspecting de-energized sections of its grid prior to re-energization, but by 2023, Liberty expects to have processes in place to inspect the grid before re-energizing and defined policies for the role of workers in suppressing ignitions.

Liberty’s WMP highlights the challenge that resource constraints have on its ability to implement wildfire mitigation activities, including retaining qualified personnel. For example, Liberty identifies the high cost of living in the Tahoe area as a constraint on available labor but does not provide a recruitment strategy.

Without a clear understanding of its risk profile to inform decision-making, Liberty may not be able to determine how to deploy wildfire mitigation initiatives in a way that maximizes risk reduction given its limited resources. Given the constraints of labor shortages, a risk-informed approach will be critical for Liberty to maximize the risk reduction it can achieve given labor constraints and ensure its highest-risk areas are being sufficiently addressed.

Resource Allocation Methodology

While the WSD’s assessment of the 2020 WMP does not approve cost recovery for its initiatives, which will be addressed in each utility’s General Rate Case or application under Public Utilities Code Section 8386.4(b)(2), the assessment does consider the effective use of resources to reduce wildfire ignition risk. Liberty relies on its Enterprise Risk Management practices and has not developed a resource allocation or risk assessment methodology specific to the wildfire threat. Liberty does not discuss RSE on a mitigation by mitigation basis, which raises questions about how Liberty can determine how to allocate its limited resources to reduce the most risk.

Liberty also does not provide a detailed justification of how it determined its portfolio of planned initiatives to be the most effective use of its resources. In order to improve decision-making going forward, Liberty will need to better understand its risk profile and track the effectiveness of mitigation initiatives to inform planning. For example, Liberty needs more sophisticated risk assessment and resource allocation methodologies related to wildfire risks to analyze grid hardening projects. The utility currently lacks a thorough tracking and analytical capability for ignition probability and various mitigation activities, and it does not employ a risk-based decision-making framework. Per its Maturity assessment, Liberty expects growth across many capabilities, yet acknowledges limited resources, raising the question of whether its planned growth—though needed to improve outcomes—is achievable. For example, by 2023, Liberty expects to have an accurate understanding of RSE for hardening initiatives but does not clearly explain how it will achieve this goal in its WMP.

A detailed discussion of the above concerns, as well as, further analysis of Liberty’s WMP is articulated in the associated Resolutions, including a complete list of deficiencies and conditions in Appendix A of the associated Resolution for Liberty.

Conclusion

Catastrophic wildfires remain a serious threat to the health and safety of Californians. Electric utilities, including, must continue to make progress toward reducing utility-related wildfire risk. Through the conditional approval granted for its 2020 WMP submission, the WSD will ensure Liberty is held accountable to successfully executing the wildfire risk reduction initiatives articulated in its 2020 WMP and required updates.

The WSD expects Liberty to meet the commitments in its 2020 WMP and fully comply with the conditions listed in Appendix A of its associated Resolution to ensure it is driving meaningful reduction of utility-related wildfire risk within its service territory.

Sincerely,

/s/  CAROLINE THOMAS JACOBS

Caroline Thomas Jacobs

Director, Wildfire Safety Division

California Public Utilities Commission

PUBLIC UTILITIES COMMISSION OF THE STATE OF CALIFORNIA

Resolution WSD-007

Wildfire Safety Division

[Date]

Resolution

RESOLUTION WSD-007 Ratifying Action of the Wildfire Safety Division on Liberty Utilities’ (CalPeco Electric) 2020 Wildfire Mitigation Plan Pursuant to Public Utilities Code Section 8386.

This Resolution ratifies the attached action of the Wildfire Safety Division (WSD) pursuant to Public Utilities Code Section 8386.  The California Public Utilities Commission’s (Commission) and the WSD’s most important responsibility is ensuring the safety of Californians.  Since several catastrophic wildfires in the San Diego area in 2007, the equipment of large electric utilities the Commission regulates has been implicated in the most devastating wildfires in our state’s history.  California’s Legislature enacted several legislative measures requiring electrical corporations to submit, and the Commission and the WSD to review, approve or otherwise act on Wildfire Mitigation Plans (WMPs) designed to reduce the risk of utility-caused catastrophic wildfire.  Key among the legislative measures are Senate Bill 901 (2018), Assembly Bill 1054 (2019), and Assembly Bill 111, discussed in detail below.

This Resolution (along with several others concurrently being issued with regard to all Commission-regulated electric utilities and independent transmission owners), acts on the WMP submitted on February 7, 2020, of Liberty Utilities/CalPeco Electric (Liberty). Liberty’s 2020 WMP responds to a list of 22 requirements set forth in Public Utilities Code 8386 and focuses on measures the electrical corporation will take over the next three years to reduce the risk of, and impact from, a catastrophic wildfire caused by its electrical infrastructure and equipment.

Electrical infrastructure and equipment pose ongoing risks of starting wildfires due to the presence of electric current.  There are three elements required to start a fire:  fuel (such as dry vegetation), oxygen, and an ignition source (heat).  A spark from electrical infrastructure and equipment can provide the ignition point from which a wildfire can spread and cause catastrophic harm to life, property, and the environment.

WMPs contain an electrical corporation’s detailed plans to reduce the risk of its equipment, operations or facilities igniting a wildfire.  This Resolution ratifies the attached action of the WSD, which has conditionally approved Liberty’s 2020 WMP in its Action Statement.  In doing so, this Resolution analyzes the extent to which Liberty’s wildfire mitigation efforts objectively reduce wildfire risk, drive improvement, and act as cost effectively as possible.  In conducting this evaluation, the Commission considers and incorporates input from the Wildfire Safety Advisory Board, the public and other stakeholders.

PROPOSED OUTCOME:

- Ratifies the attached action of the WSD to approve the 2020 WMP of Liberty, with conditions designed to ensure WMP decreases risk of catastrophic wildfire in California.

- A list of conditions of approval is in Appendix A.

- Evaluates the maturity of Liberty’s WMP using the WSD’s new Utility Wildfire Mitigation Assessment, as represented in the Utility Wildfire Mitigation Maturity Model. Final maturity model outputs should be viewed as levels or thresholds – they are not absolute scores.

- Requires Liberty to file an update to its WMP in 2021 according to a forthcoming schedule to be released by the WSD.

- Does not approve costs attributable to WMPs, as statute requires electrical corporations to seek and prove the legitimacy of all expenditures at a future time in their General Rate Cases (GRC) or compliant application.  Nothing in this Resolution nor the WSD’s Action Statement should be construed as approval of any WMP-related costs.

- Does not establish a defense to any enforcement action for a violation of a Commission decision, order, or rule.

SAFETY CONSIDERATIONS:

Mitigation of catastrophic wildfires in California is among the most important safety challenges the Commission-regulated electrical corporations face.  Comprehensive WMPs are essential to safety because:

- WMPs list all of an electrical corporation’s proposed actions to reduce utility-related wildfire risk and prevent catastrophic wildfires caused by utility infrastructure and equipment. By implementing measures such as vegetation management, system hardening (such as insulating overhead lines and removing or upgrading equipment most likely to cause fire ignition), improving inspection and maintenance, situational awareness (cameras, weather stations, and use of data to predict areas of highest fire threat), improving community engagement and awareness, and other measures, utility-caused catastrophic wildfire risk should be reduced over time.

- The WSD’s and Commission’s substantive and procedural changes for evaluations of electrical corporations’ 2020 WMPs will enhance California’s ability to mitigate catastrophic wildfire risk related to utilities.  Below is a summary of the key, new requirements in the 2020 process, required of all WMP filers:

  - A WMP template and format so WMPs are standardized and include similar information in the same format.

  - Standard data submissions, in spatial, non-spatial and tabular format, which grounds the WMPs in specific data.  Data submissions will continue throughout the WMP 3-year horizon and be used to measure compliance and performance to program, progress and outcome metrics.

  - A new Utility Survey that objectively assesses the electrical corporation’s maturity across 52 capabilities in 10 categories. The resulting Maturity Matrix quantitatively presents the progressive impact of the electrical corporation’s wildfire mitigation plan activities over the WMP 3-year horizon.

ESTIMATED COST:

- Nothing in this Resolution should be construed as approval of the costs associated with the WMP mitigation efforts.

- For illustrative purposes, Table 1 below contains filer’s estimates of its projected costs for the wildfire mitigation efforts in its 2020 WMP.

- Liberty may not record the same costs more than once or in more than one place, seek duplicative recovery of costs, or record or seek to recover costs in the memorandum account already recovered separately.  All electrical corporations should ensure they carefully document their expenditures in these memorandum accounts, by category, and be prepared for Commission review and audit of the accounts at any time.

Table 1: Proposed WMP costs

| Proposed WMP costs |  |
| --- | --- |
| Total costs 2020-2022 | $88 million |
| Subtotal: 2020 | $30 million |
| Subtotal: 2021 | $32 million |
| Subtotal: 2022 | $27 million |

Table of Contents

Summary	1

1.	Background	1

2.	Notice	3

3.	Wildfire Safety Division Analysis of WMP	3

4.	Wildfire Safety Advisory Board Input	5

5.	Public and Stakeholder Comment	5

6.	Discussion	8

6.1.	Persons Responsible for Executing The Plan	9

6.2.	Metrics and Underlying Data	9

6.3.	Baseline Ignition Probability and Wildfire Risk Exposure	11

6.4.	Inputs to the Plan, Including Current and Directional Vision for Wildfire Risk Exposure	12

6.5.	Wildfire Mitigation Activity for Each Year of the 3-Year WMP Term, Including Expected Outcomes of the 3-Year Plan	14

6.5.1.	Risk Assessment and Mapping	15

6.5.2.	Situational awareness and forecasting	16

6.5.3.	Grid Design and System Hardening	17

6.5.4.	Asset Management and Inspections	20

6.5.5.	Vegetation Management and Inspections	20

6.5.6.	Grid Operations and Operating Protocols	22

6.5.7.	Data Governance	23

6.5.8.	Resource Allocation Methodology	24

6.5.9.	Emergency Planning and Preparedness	25

6.5.10.	Stakeholder Cooperation and Community Engagement	26

7.	Maturity Evaluation	26

8.	Impact of COVID-19 Pandemic	29

9.	Conclusion	30

10.	Comments	30

Findings	30

THEREFORE, IT IS ORDERED THAT:	31

Appendix A – Deficiencies and Conditions

Appendix B – Detailed Figures & Charts

Appendix C – Maturity Model Summary

Appendix D – Definition of Mitigation Initiatives

Appendix E – Public Utilities Code Section 8386

Summary

This Resolution acts on the attached Wildfire Safety Division’s (WSD’s) conditional approval of the WMP submitted by Liberty Utilities/CalPeco Electric (Liberty) on February 7, 2020.  The Resolution finds that Liberty is in compliance with the requirements for WMPs set forth in Assembly Bill (AB) 1054, codified at Public Utilities Code (Pub. Util. Code) Section 8386(c) and the WMP Guidelines issued by the Commission to electrical corporations.  Section 8386 requires that electrical corporations’ WMPs contain 22 elements; the full list of elements appears in Appendix E to this Resolution.

There are three possible actions for the WSD and Commission in response to any electrical corporation’s WMP:  approval, denial, or approval with conditions.  In the case of the WMP resolved here, we ratify the WSD’s action to approve the WMP with conditions.  To the extent we do not impose conditions on elements of the WMP, that element is approved.

The list of conditions of approval is in Appendix A.

Background

Catastrophic wildfires in 2017-19 led the California Legislature to pass Senate Bill (SB) 901 in 2018 and its successor AB 1054 in 2019, as well as AB 111.  SB 901 and AB 1054 contain detailed requirements for electrical corporations’ WMPs and provide a 90-day review cycle of WMPs by the WSD.  AB 111 establishes a new division, the WSD, within the Commission.  The duties of the WSD are contained in Pub. Util. Code Section 326(a), including to evaluate, oversee and enforce electrical corporations’ compliance with wildfire safety requirements, and develop and recommend to the Commission performance metrics to achieve maximum feasible wildfire risk reduction.  SB 901 required a formal Commission proceeding for WMP review in 2019, and to that end the Commission reviewed the 2019 WMPs in Rulemaking (R.) 18-10-007.  The decisions dispensing of the 2019 WMPs also added additional requirements for the 2020 WMPs.

After the Commission issued its WMP decisions on May 30, 2019, the Legislature enacted AB 1054.  AB 1054 contains similar WMP requirements to SB 901 but allows WMPs a three-year rather than one-year duration.  AB 1054 also requires the WSD to review and approve, deny or approve with conditions the electrical corporations’ WMPs, with Commission ratification to follow thereafter.  AB 1054 also requires establishment of a Wildfire Safety Advisory Board (WSAB), with appointees from the California Governor and Legislature, to provide comments on the 2020 WMPs and develop and make recommendations related to the metrics used to evaluate WMPs in 2021 and beyond.

Building on lessons learned from the WMP review process in 2019, the WSD developed and required all electrical corporations to conform their WMPs to a set of new WMP Guidelines starting in 2020.  For 2020, the WMP Guidelines add requirements on detail, data, and other supporting information. The WMP Guidelines are designed 1) to increase standardization of information collected on electrical corporations’ wildfire risk exposure, 2) enable systematic and uniform review of information each electrical corporation submits, and 3) move electrical corporations toward an effective long-term wildfire mitigation strategy, with systematic tracking of improvements over time.

The Commission adopted Resolution WSD-001 setting forth the process for the WSD and Commission review of the 2020 WMPs.  The resolution called for electrical corporations to submit their 2020 WMPs on February 7, 2020.  Liberty submitted its WMP on that date, and in response to several data requests from the WSD, it filed an amended WMP on February 28, 2020.  This amended filing contained all of the required elements of Sec. 8386 (a) and addressed each of the Guidelines, although some elements will require additional information as detailed in the body of this resolution.

Shortly after electrical corporations filed their WMPs, the WSD held two sets of all-day workshops over four days, on February 18, 19, 24 and 25.  The February 18-19, 2020, informational workshops called for the electrical corporations to present to stakeholders and the public details on their WMPs, and for stakeholders to ask questions, raise concerns, and otherwise comment on the WMPs’ contents.  The February 24-25 technical workshops focused more in depth on key provisions of the WMPs:  vegetation management, system hardening, risk-spend efficiency emerging technology and reduction of the scale and scope of Public Safety Power Shutoff (PSPS) events.  Again, stakeholder and public input was offered.

Stakeholders were also allowed to submit comments on the WMP, to which the electrical corporation replied.  Stakeholders and members of the public commented on the WMPs by April 7, 2020, and the electrical corporations responded to those comments by April 16, 2020.

Notice

In accordance with Pub. Util. Code § 8386(d), notice of Liberty’s WMP was given by posting of the WMP on the WSD’s webpage, at www.cpuc.ca.gov/wildfiremitigationplans, on February 7, 2020, in accordance with the requirements of Pub. Util. Code Section 8386(d).  Further, the electrical corporation served its 2020 WMP on the Commission’s existing WMP formal proceeding (R.18-10-007) service list, as Resolution WSD-001 provided.  Resolution WSD-001 also required the filer to post all data request responses, as well as any document referenced in its WMP, on its own website and update the website with notice to the R.18-10-007 on a weekly basis.

Wildfire Safety Division Analysis of WMP

To reach a conclusion about each WMP, the WSD reviewed each electrical corporation’s 2020 WMP (including updates and Geographic Information System (GIS) data), public and WSAB input, responses to WSD data requests, and responses to the maturity model survey questions. For Liberty, the WSD issued three sets of data requests for missing information, clarification, and supplementation where necessary. The initial set of data requests were to ensure completeness of compliance with all of the elements of WMPs required by Sec 8386.  Subsequent data requests were to obtain additional information, especially for use in GIS analysis by CAL FIRE. Upon completion of this review, the WSD determined whether each utility’s 2020 WMP should either approved without conditions, approved with conditions, or denied.

There are three possible actions for the WSD in response to any electrical corporation’s WMP: approval, denial, or approval with conditions. To reach its conclusion, the WSD reviewed the WMPs for compliance with every aspect of the WMP Guidelines and AB 1054 and requirements of the 2019 WMP Decisions.  The WSD designed the WMP Guidelines to require that each filer have a comprehensive WMP that contains all elements required by AB 1054. Thus, for example, every WMP must contain plans for vegetation management, system hardening, inspections of assets and vegetation, situational awareness, a plan to reduce and manage PSPS events, customer and first responder outreach and coordination, risk analysis, GIS data, a short- and long-term vision, analysis of causes of ignition, and many other elements.  To evaluate WMPs, the WSD assessed each plan for its completeness, the technical feasibility and effectiveness of its initiatives, whether proposed initiatives were an efficient use of resources, and for demonstration of a sufficiently growth-oriented approach to reducing utility-related wildfire risk over time.

A conditional approval explains each missing or inadequate component in the WMP. The 2020 WMP Resolutions for each electrical corporation contain a set of “Deficiencies “and associated “Conditions” to remedy those deficiencies.  Each deficiency is categorized into one of the following categories, with Class A being the most serious:

- Class A – aspects of the WMP are lacking or flawed;

- Class B – insufficient detail or justification provided in WMP;

- Class C – gaps in baseline or historical data, as required in 2020 WMP Guidelines.

Class A deficiencies are of the highest concern and require an electrical corporation to develop and submit to the WSD within 45 days of Commission ratification of this Resolution, a Remedial Compliance Plan (RCP) to resolve the identified deficiency.  Class B deficiencies are of medium concern and require reporting by the electrical corporation to provide missing data or update its progress in its quarterly report. Such reporting will be either on a one-time basis or ongoing as set forth in each condition. Class C deficiencies require the electrical corporation to submit additional detail and information or otherwise come into compliance in its 2021 annual WMP update. Detailed descriptions of the RCP and quarterly reports are contained in Resolution WSD-002, the Guidance Resolution on 2020 Wildfire Mitigation Plans.

The WSD’s key concerns relate to the following aspects of the WMP:

While Liberty has shown a strong response in evolving its WMP by identifying and addressing lessons learned from recent experience, it still lacks a thorough tracking and analytical capability for ignition probability and various mitigation activities, and it does not employ a risk-based decision-making framework.  The utility intends to develop a Fire Prevention Index (FPI) which could help provide a basis for improved use of data and metrics. It has not fully explained or justified certain mitigation proposals, especially for expensive grid hardening and undergrounding projects.

Liberty plans to allocate approximately a quarter of its total planned spend on installation of covered conductor. Liberty plans to steadily increase its covered conductor program through the plan cycle and intends to ultimately replace all overhead primary distribution conductors with covered conductor in the decade to come. Additionally, Liberty plans to allocate approximately another quarter of its budget to vegetation management initiatives, including remediation of at-risk species (16 percent) and fuel management work (8 percent). See Appendix B, Figure 3.7.

Liberty needs to improve its analysis of ignition probabilities, focusing on the causes of known near-miss events and causes of an apparent increasing trend in outages/faults.

This Resolution discusses and resolves these issues below.

Wildfire Safety Advisory Board Input

The WSAB provided recommendations on the WMPs of Pacific Gas and Electric Company (PG&E), Southern California Edison Company (SCE), and San Diego Gas & Electric Company (SDG&E) on April 15, 2020. Although not focusing specifically on Liberty’s WMP, the WSD has considered the WSAB’s recommendations, and this Resolution incorporates WSAB’s input throughout.

The WSAB focused its recommendations on high-level input and identification of shortcomings in the 2020 WMPs to inform upcoming wildfire mitigation efforts. WSAB recommendations focused on the following areas:  vegetation management and inspection; grid design and system hardening; resource allocation methodology; and PSPS preparation, including communication with the community, planning, and recovery after PSPS events.

Public and Stakeholder Comment

The following individuals and organizations submitted comments specific to Liberty’s WMP:  California Public Advocates Office, Joint Local Governments/Rural Counties and Green Power Institute. Several other stakeholders provided comments that were targeted to the three large electrical corporations. In some cases, especially from The Utility Reform Network (TURN) and Energy Producers & Users Coalition (EPUC), comments directed towards other utilities could also be applied to Liberty and the other Small and Multi-Jurisdictional Utilities (SMJUs).

Many stakeholders found the WMPs lacking in specific and complete data, especially related to Risk Spend Efficiency (RSE). Generally, stakeholders also found comparing utilities difficult due to inconsistent reporting across utilities. The utilities received some appreciation for the general expansion of programs, with some stakeholders noting specific improvements in situational awareness. Many also reiterated that approval of the WMPs neither approves the scope nor portfolio of programs nor authorizes rate recovery.

The Utility Reform Network (TURN)

- Compliance inspection and repair programs should not be deemed new activities.

- Use of Light Detection and Ranging (LiDAR) technology for situational awareness.

- Covered Conductor Circuit Targeting

Green Power Institute (GPI)

- Liberty and the other SMJUs should catch up to the larger electrical corporations in use of analytical tools and mitigation measures.  A need exists for improvement including in the following areas:

  - Development of a risk-based decision-making framework, including RSE values and thorough risk bowtie analyses;

  - Establishment of more comprehensive, “living-document” tools, methods, and protocols;

  - Adoption of digitized versus paper forms and advanced system tracking;

  - Assessment of run-to-failure asset replacement schedules and their impact on wildfire risk;

  - Vegetation management compliance and consideration of enhanced vegetation management that goes beyond simple regulatory compliance;

  - Integration of mature wildfire modeling tools;

  - Development of a more comprehensive customer communication and outreach program and concrete plans for providing support for affected customers (e.g., back-up generation, community support centers); and

  - Examination of whether the rate of system hardening and increased system resiliency upgrades is adequate to reduce wildfire risk

  - Need for better RSE data

  - Use of microgrids

  - Equipment replacement thresholds

  - Vegetation management tracking systems

  - Recommends better stakeholder and community engagement, including outreach

  - Suggests directing residual wood waste created by tree trimming and felling to biomass plants (an issue that is not a subject of the 2020 WMPs)

Rural Counties of California Representatives (RCRC)/Joint Local Governments

- Liberty did not sufficiently consider undergrounding of power lines as a system-hardening option.

- Liberty should consider use of Expulsion Fuse Replacements

- Liberty should consider improved vegetation management in future plans.

Energy Producers and Users Coalition (EPUC)

- Need to include RSE data

Public Advocate’s Office of the Public Utilities Commission (Cal Advocates)

- Liberty provides insufficient GIS data, and should make “substantial improvements” to the utility’s GIS data responses, including clearly labelling data in Liberty’s 2021 WMP Update

On April 16, 2020, Liberty submitted reply comments, in which the utility committed to providing improved geospatial data in the future, and to consider the results of its asset inventory survey in its 2021 WMP.  Liberty also notes in response to the RCRC comments that the company considered undergrounding in developing its WMP.

Discussion

The Commission has reviewed the actions taken by the Wildfire Safety Division (WSD) pursuant to Public Utilities Code section 8386.3, the recommendations of Wildfire Safety Advisory Board (WSAB), stakeholder comments served on the R.18-10-007 service list, the underlying documents, and other public input.

Despite its small territory and limited resources, Liberty appears to be making necessary efforts to implement processes and reporting procedures that will make its wildfire mitigations effective and enhance Liberty’s accountability.  Liberty provides a preliminary description of such processes in its 2020 Wildfire Mitigation Plan (WMP), even if they are not yet fully operational.

Liberty projects an expansion of its weather station network and deployment of Distribution Automation Controls. This expansion will improve fault detection and enhance Liberty’s ability to forecast weather events and inform decision-making regarding potential Public Safety Power Shutoff (PSPS) events.  Additionally, Liberty describes a program for replacing reclosers, which is an improvement upon the existing system.

The following aspects of the WMP raise concerns:

- Liberty’s inspections and vegetation management programs are compliance-based and designed to meet minimum requirements within the Commission’s General Orders. They are not risk-informed to drive wildfire mitigation.  For example, Liberty proposes to maintain a three-year cycle of inspections, except in Tier 3 High Fire Threat District (HFTD).  However, a three-year cycle may be inadequate to meet the State’s increasing wildfire risks.

- Liberty is developing a risk assessment and resource allocation program that will improve its ability to address wildfire risk. However, Liberty does not expect to have a refined process in place before its next general rate case filing.

- Liberty’s data governance program is in the very early stages of development.  As noted by the Public Advocates Office, Liberty’s Geographic Information System (GIS) data and asset inventory requires improvement in the 2021 WMP filing.  Liberty should confer with CAL FIRE and the WSD to fill in gaps in its GIS data in preparation for its 2021 WMP Update.

- Although its history of ignitions caused by utility equipment is limited, Liberty’s data  provided in response to a data request indicates that Liberty anticipates moderate to significant increases in the trends of several of its top ignition drivers over the next decade. Liberty needs to improve its analysis of ignition probabilities, focusing on the causes of known near-miss events and causes of an apparent increasing trend in outages/faults.

- Because its resources devoted to wildfire risk mitigation are limited, Liberty’s decision to invest in a costly undergrounding project at $6 million/mile in 2021 when it does not anticipate completing its less costly expulsion fuse replacement program until 2026 raises concerns. The lack of Risk Spend Efficiency (RSE) and resource allocation analysis raises questions about Liberty’s priorities and makes it difficult to evaluate its choices.

Therefore, the WSD’s approval of Liberty’s WMP is conditioned on Liberty’s compliance with each of the “conditions” set forth in Appendix A, and associated conditions addressed in the Guidance Resolution, WSD-002.

The following sections discuss in detail the Liberty’s WMP, its contents, required changes, and conditions imposed on approval.  The discussion follows the template provided in WMP Guidelines attached to the R.18-10-007 Administrative Law Judge’s December 16, 2019 ruling as Attachment 1.

Persons Responsible for Executing The Plan

This section of the WMP requires that the filer designate a company executive with overall responsibility for the plan, and program owners specific to each component of the plan.  The section also requires a senior officer to verify the contents of the plan, and the filer to designate key personnel responsible for major areas of the WMP.

Liberty provided the required information.

Metrics and Underlying Data

The metrics and underlying data section of the WMP represents an innovation over the 2019 WMP requirements in that all filers are required to report standardized and normalized data on many aspects, including their performance metrics, conditions in their service territories, grid topology, and wildfire mitigation efforts.  To remedy a concern with the 2019 plans, the 2020 WMP Guidelines disallow the practice of filers characterizing only "program targets" (e.g., number of miles of covered conductor installed or trees trimmed) as the "metrics" required by the statute.10  For 2020, the WMP Guidelines require filers to group metrics and program targets as follows.

- Progress metrics track how much electrical corporation wildfire mitigation activity has managed to change the conditions of electrical corporation’s wildfire risk exposure in terms of drivers of ignition probability.

- Outcome metrics measure the performance of an electrical corporation and its service territory in terms of both leading and lagging indicators of wildfire risk, PSPS risk, and other direct and indirect consequences of wildfire and PSPS, including the potential unintended consequences of wildfire mitigation work.

- Program targets measure tracking of proposed wildfire mitigation activities against the scope and pace of those activities as laid out in the WMPs but do not track the efficacy of those activities.  The primary use of these program targets in 2020 will be to gauge electrical corporation follow-through on WMPs.

This section first requires filers to discuss how the their plans have evolved since 2019, outline major themes and lessons learned from implementation of their 2019 plan and discuss how the filers performance against metrics used in their 2019 plans have informed their 2020 WMP.  A series of tables then requires reporting of recent performance on predefined outcome and progress metrics,  including numbers of ignitions, near misses, PSPS events, worker and public deaths and injuries, acreage affected, and assets destroyed by fire, and critical infrastructure impacts, as well as additional metrics the filer proposes to use to ensure the effectiveness of its efforts in quantitatively mitigating the risk of utility-caused catastrophic wildfire.  This section also requires filers to detail their methodology for calculating or modeling potential impact of ignitions, including all data inputs used, data selection and treatment methodologies, assumptions, equations or algorithms used and types of outputs produced.  Finally, this section requires filers to provide a number of GIS files detailing spatial information about their service territory and performance, including recent weather patterns, location of recent ignitions, area and duration of PSPS events, location of lines and assets, geographic and population characteristics and location of planned initiatives.

Appendix B, Figure 2.2b depicts near misses normalized by circuit miles and Appendix B, Figure 2.3b depicts normalized ignitions. Appendix B, Figure 2.6b provides a detailed breakdown of ignitions by driver. It is important to consider these data in conjunction to better understand the scope, frequency, and scale of the drivers of utility ignition. Presumably, there are relationships between near misses and ignitions that can better inform utility performance and track progress.

From 2015 to 2018, Liberty reports almost no fluctuation in near misses per circuit mile; however, in 2019 Liberty reports a 160 percent increase in near miss incidents. The majority of Liberty’s 2019 increase in near miss incidents is driven by “object contact,” “wire-to-wire contact,” and “other” categories. In Liberty’s case, there does not seem to be a correlation between its increase in near miss incidents and ignitions, as it reported no ignitions for two of the five reporting years (2017 and 2018).

A substantial increase in “near misses” signals a trend that could in the future lead to increased ignitions.

A detailed analysis and comparison across peer utilities is provided in 
Appendix B.

Baseline Ignition Probability and Wildfire Risk Exposure

The baseline ignition probability and wildfire risk exposure section of the WMP requires electrical corporations to report baseline conditions and recent information related to weather patterns, drivers of ignition probability, use of PSPS, current state of utility equipment, and summary data on weather stations and fault indicators. The section then requires the filer to provide information on its planned additions, removals, and upgrades of equipment and assets by the end of the 3-year plan term, in urban, rural and highly rural areas.  The information must describe the scope of hardening efforts (i.e., circuit miles treated), distinguish between efforts for distribution and transmission assets, and identify certain locational characteristics (i.e., urban, rural and highly rural) of targeted areas.  Filers must also report the sources of ignition over the past 5 years due to ignition drivers outlined in the annual fire incident data collection report template adopted in D.14-02-015.

Considering that managing the potential sources of ignition from its infrastructure, operations, and equipment is the single most controllable aspect of utility wildfire risk, understanding the sources and drivers of near misses and ignitions is one of the most critical capabilities in reducing utility-caused wildfire risk.  Moreover, it is important to consider these performance metrics relative to annual fluctuations in weather conditions (i.e., incidence of Red Flag Warning (RFW) days, days with high wind conditions – 95th and 99th percentile winds, and high fire potential days measured relative to utility FPIs or other fire danger rating systems) to better gauge relationships and thresholds between weather and fire potential indicators and utility ignitions.  As such, the discussion in this section focuses on recent weather patterns, key drivers of utility ignitions and frequencies of such ignitions, recent use of PSPS, the current baseline conditions of the utility’s service territory and equipment, and locations of planned utility upgrades.

Because Liberty reported an average of just one (1) ignition per year over the past five years, it is difficult to discern trends related to causation.  Contact from objects (including both vegetation and other objects) and equipment failure are the documented causes of historical ignitions, though Liberty also reports one ignition due to “other” causes.  Although its history of ignitions caused by utility equipment is limited, its response to a WSD data request indicates that Liberty anticipates moderate to significant increases in the trends of several of its top ignition drivers over the next decade.

A detailed summary and comparison of performance metrics and current state of utility service territories is provided in Appendix B.

Inputs to the Plan, Including Current and
Directional Vision for Wildfire Risk Exposure

This section of the WMP requires the filer to rank and discuss trends anticipated to exhibit the greatest change and have the greatest impact on ignition probability and wildfire consequence, within the filer’s service territory, over the next 10 years.  First, filers must set forth objectives over the following timeframes:  Before the upcoming wildfire season, before the next annual update, within the next 3 years, and within the next 10 years.

Filers must describe how the utility assesses wildfire risk in terms of ignition probability and estimated wildfire consequence, using Commission adopted risk assessment requirements (for large electrical corporations) from the GRC Safety Model and Assessment Proceeding (S-MAP) and Risk Assessment Mitigation Phase (RAMP).  The filer must describe how the utility monitors and accounts for the contribution of weather and fuel to ignition probability and wildfire consequence; identify any areas where the Commission’s High Fire Threat District (HFTD) should be modified; and rank trends anticipated to have the greatest impact on ignition probability and wildfire consequence.

A key area which filers are required to address is Public Safety Power Shutoffs (PSPS). In 2019 electrical corporations proactively shutoff power to millions of customers for multiple days, resulting in numerous cascading consequences, including associated public safety concerns.  The Commission has been clear in its judgement that those events were unacceptable and cannot be repeated.   The new 2020 WMP Guidelines direct the electrical corporations to describe lessons learned from past PSPS events and quantify the projected decrease of circuits and customers affected by PSPS as a result of implementing wildfire mitigation programs and strategies contained in the WMP.

Liberty has experienced only one PSPS event, in 2018, which was narrow in scope, affecting just a single circuit and resulting in a total 90 hours of customer outages. Liberty did not experience a PSPS event in 2019, but it stated that there was a single instance when it did initiate the processes and ultimately determined a PSPS event was unnecessary. The PSPS framework reportedly helped Liberty develop better decision-making processes and communication plans.

Given its relatively small territory and few customers Liberty did not analyze future quantitative impacts of the number of customers and circuits affected by PSPS events.  Liberty does not have a set process as it relates to the PSPS program and serving customers in urban, rural, and highly rural areas.  Moving forward, Liberty said it will study possible differences in approaches to PSPS protocols across the customer classes in the Wildland Urban Interface (WUI) designation.

Wildfire Mitigation Activity for Each Year of the 3-Year WMP Term,
Including Expected Outcomes of the 3-Year Plan

This section of the WMPs is the heart of the plans and requires the filer to describe each mitigation measure it will undertake to reduce the risk of catastrophic wildfire caused by the utility’s infrastructure, operations, and equipment.  A description of each type of measure appears below, with elaboration in Appendix D to this Resolution.

First, the WMP Guidelines require a description of the overall wildfire mitigation strategy over the following timeframes: before the upcoming wildfire season, before the next annual update, within the next 3 years and within the next 
10 years.  The filer is required to describe its approach to determining how to manage wildfire risk (in terms of ignition probability and estimated wildfire consequence) as distinct from other safety risks.  The filer is required to summarize its major investments over the past year, lessons learned, and changes planned for 2020-2022; describe challenges associated with limited resources; and outline how the filer expects new technologies to help achieve reduction in wildfire risk.

Next, Section 5 requires the filer to explain how it will monitor and audit the implementation of the plan and lay out the data the filer relies on in operating the grid and keeping it safe.  It then requires detailed descriptions of specific mitigations or programs, in the following order:

- Risk assessment and mapping

- Situational awareness and forecasting

- Grid design and system hardening

- Asset management and inspections

- Vegetation management and inspections

- Grid operations and operating protocols

- Data governance

- Resource allocation methodology

- Emergency planning and preparedness

- Stakeholder cooperation and community engagement.

Below, this Resolution evaluates the mitigations (or initiatives) Liberty proposed for each of the 10 foregoing categories.  After identifying each proposed mitigation or group of mitigations, the Resolution discusses concerns with the proposal, and identifies any conditions imposed.  Provided in Appendix B, for illustrative purposes, are summaries of the filer’s projected costs across highest total cost initiatives as well as projected costs across the highest category initiatives.

Liberty’s top five initiatives by planned spend are found on Appendix B, Figure 3.7.  Liberty plans to allocate approximately a quarter of its total planned spend on installation of covered conductor. Liberty plans to steadily increase its covered conductor program through the plan cycle and intends to ultimately replace all overhead primary distribution conductors with covered conductor in the decade to come. Additionally, Liberty plans to allocate approximately another quarter of its budget to vegetation management initiatives, including remediation of at-risk species (16 percent) and fuel management work (8 percent).

Risk Assessment and Mapping

This section of the WMP requires the filer to discuss the risk assessment and mapping initiatives implemented to minimize the risk of its equipment causing wildfires.  Filers must describe initiatives related to maps and modelling of overall wildfire risk, ignition probability, wildfire consequence, risk-reduction impact, match-drop simulations, and climate/weather driven risks.  This section also requires the electrical corporation to provide data on spending, miles of infrastructure treated, spend per treated line mile, ignition probability drivers targeted, projected risk reduction achieved from implementing the initiative, RSE, and other (i.e., non-ignition) risk drivers addressed by the initiative.

Liberty does not currently have the tools or models necessary for risk mapping. The utility stated that it is in the process of developing a risk mapping tool that would provide the ability to conduct dynamic analysis of incident reporting by overlaying various maps of the utility territory. This software will be able to show ignition probability by circuit.

Climate/weather driven risk mapping, initiative mapping and PSPS risk reduction impacts are all on the company’s agenda before its next General Rate Case in 2021 and would be included in the next WMP cycle.  As noted by the Public Advocates Office, Liberty’s GIS data and asset inventory requires improvement in the 2021 WMP filing.  

Deficiencies and Conditions - Risk assessment and mapping

While vague as to timelines beyond next year, Liberty said it will continue to evaluate its risk mapping capability and make refinements as warranted. Although it states its near-term intentions in specific terms, Liberty does not provide much detail on how it expects to use the risk mapping capability in its decision-making or how it will evaluate effectiveness. Liberty also did not provide any cost estimates for this initiative.

Deficiencies such as these are not unique to Liberty.  As such, this deficiency and associated condition is addressed in the Guidance Resolution, WSD-002.

Situational Awareness and Forecasting

The situational awareness and forecasting section of the WMP requires the filer to discuss its use of cameras, weather stations, weather forecasting and modeling tools, grid monitoring sensors, fault indicators, and equipment monitoring.  Situational awareness requires the electrical corporation to be aware of actual ignitions in real time, and to understand the likelihood of utility ignitions based on grid and asset conditions, wind, fuel conditions, temperature and other factors.

The WMP Guidelines refer to key situational awareness measures, including:

- Installation of advanced weather monitoring and weather stations that collect data on weather conditions so as to develop weather forecasts and predict where ignition and wildfire spread is likely,

- Installation of high definition cameras throughout an electrical corporation’s service territory, with the ability to control the camera’s direction and magnification remotely,

- Use of continuous monitoring sensors that can provide near real-time information on grid conditions,

- Use of a fire risk or fire potential index that takes numerous data points in given weather conditions and predicts the likelihood of wildfire, and

- Use of personnel to physically monitor areas of electric lines and equipment in elevated fire risk conditions.

Liberty’s situational awareness plans consist of 10 weather stations installed in 2019 plus an additional 40 weather stations by 2021, featuring fuel moisture and precipitation sensors.  It is also in the process of developing a Fire Potential Index (FPI), a utility best practice, which it expects to be fully functional before the upcoming wildfire season.

These initiatives will support more advanced weather forecasting and help evaluate the need for PSPS events. In 2019, Liberty contracted to develop weather monitoring and notification tools to warn of potential elevated fire risks.

In addition, Liberty is installing Distribution Fault Anticipation sensors to identify line failure events that could precipitate ignitions.

The electrical corporation’s strengths lie in pursuing several sophisticated measures not typical of smaller utilities. Its plan to expand weather stations throughout its territory illustrates forward thinking strategy, and its development of the tools to use data from its system is appropriate.

Its $615,000 budget for advanced weather monitoring and stations from 
2020-2022 represents a continuation of its 2019 actual spending. Liberty plans a substantive investment in continuous monitoring sensors in 2021 and 2022.

Grid Design and System Hardening

The grid design and system hardening section of the WMPs examine how the filer is designing its system and what it is doing to strengthen its distribution and transmission system and substations to prevent catastrophic wildfire.  The grid design and system hardening WMP section also requires discussion of routine and non-routine maintenance programs, including whether the filer replaces or upgrades infrastructure proactively rather than running facilities to failure.  Programs in this category, which often cover the most expensive aspects of a WMP, include initiatives such as the installation of covered conductors to replace bare overhead wires, undergrounding of distribution or transmission lines, and pole replacement programs.  The filer is required, at a minimum, to discuss grid design and system hardening in each of the following areas:

- Capacitor maintenance and replacement,

- Circuit breaker maintenance and installation to de-energize lines upon detecting a fault,

- Covered conductor installation,

- Covered conductor maintenance,

- Crossarm maintenance, repair, and replacement,

- Distribution pole replacement and reinforcement, including with composite poles,

- Expulsion fuse replacement,

- Grid topology improvements to mitigate or reduce PSPS events,

- Installation of system automation equipment,

- Maintenance, repair, and replacement of connectors, including hotline clamps,

- Mitigation of impact on customers and other residents affected during PSPS event,

- Other corrective action,

- Pole loading infrastructure hardening and replacement program based on pole loading assessment program,

- Transformers maintenance and replacement,

- Transmission tower maintenance and replacement,

- Undergrounding of electric lines and/or equipment,

- Updates to grid topology to minimize risk of ignition in HFTDs, and

- Other/not listed items if an initiative cannot feasibly be classified within those listed above

Liberty’s grid design and system hardening plan is narrowly focused on an increasing effort to replace bare wire with covered conductor in the next three years.  While the number of line miles is just 26 miles, these are located in remote areas with difficult terrain.

Liberty also projects higher levels of spending for Expulsion Fuse Replacements, installations of system automation equipment, and Pole Loading Infrastructure Hardening and Replacement. Liberty also contemplates limited line undergrounding but faces significant costs in doing so. A single line-mile of undergrounding included in the WMP for 2021 is estimated at between 
$5 million and $6.1 million/mile. This compares with 4 miles of undergrounding planned for 2020 with an estimated cost of $481,000/mile or $1.75 million total.

Liberty does not have additional grid design measures that are intended to mitigate PSPS impacts. A proposed microgrid project, planned for 2020, would provide backup power to a limited number of customers.

Overall, Liberty is showing ambition to pursue a limited set of grid hardening initiatives which are appropriate for its terrain and risk profile, although relatively costly.

Deficiencies and Conditions - Grid design and system hardening

Deficiency (LIB-1, Class B): Liberty did not describe methods for tracking effectiveness of its covered conductor initiative.

Although Liberty asserts intention to extensively deploy covered conductor throughout its entire service territory, Liberty has not developed a method for tracking the effectiveness of its planned covered conductor installations or studied the structural impacts that such a broad deployment would create on the existing overhead infrastructure across its service territory.

Condition (LIB-1, Class B): In its first quarterly report, Liberty shall:

  - Describe a methodology for tracking and measuring the effectiveness of its covered conductor installations at reducing the frequency and probability of:

    - outages for top 10 outage causes based on best available historical data; and

    - ignitions for all CPUC reportable ignitions; and

  - Describe the magnitude and scope of the structural impacts of broad covered conductor deployment across its existing overhead facilities, the associated asset replacement consequences by asset type, and the estimated cost of those associated replacements.

Asset Management and Inspections

The asset management and inspections portion of the WMP Guidelines requires the filer to discuss power line/infrastructure inspections for distribution and transmission assets within the HFTD, including infrared, LiDAR, substation, patrol, and detailed inspections, designed to minimize the risk of its facilities or equipment causing wildfires.  The filer must describe its protocols relating to maintenance of any electric lines or equipment that could, directly or indirectly, relate to wildfire ignition.  The filer must also describe how it ensures inspections are done properly through a program of quality control.

Liberty’s asset management and inspection programs are largely driven by compliance with Commission General Order 165 and GO 174. Its most extensive program appears to be pole loading assessment to determine safety factors.  Rising from an actual 2019 expenditure of less than $1 million, Liberty expects to spend over $9.5 million on the program over the next three years.

About 70 percent of Liberty’s allocated funds for this area are for inspections.  Liberty is moving from paper tracking to electronic tracking of inspection findings, which is an improvement over current practice.

Vegetation Management and Inspections

This section of the WMP Guidelines requires filers to discuss vegetation inspections, including inspections that go beyond existing regulation, as well as infrared, LiDAR, and patrol inspections of vegetation around distribution and transmission lines/equipment, quality control of those inspections, and limitations on the availability of workers.  The filer must also discuss collaborative efforts with local land managers to leverage opportunities for fuel treatment activities and fire break creation, methodology for identifying at-risk vegetation, how trim clearances beyond minimum regulations are determined, and how the filer considers and addresses environmental and community impacts related to tree trimming and removal (erosion, flooding, and the like).

Liberty’s vegetation management and inspection programs consist of routine inspections along all distribution lines, and trimming/removal of vegetation to conform with required laws and regulations.  Liberty reports on page 74 of its WMP that it has 50 miles of overhead conductor in its Tier 3 HFTD and that it plans to conduct annual inspections on these lines. Separately, in Table 13, Liberty reports a total of 69 overhead circuit miles in Tier 3 HFTD in urban areas, 39 miles in rural areas, and 16 miles in highly rural areas for a total of about 
123 circuit miles of overhead distribution in HFTD Tier 3.

Liberty plans to allocate approximately one quarter of its total mitigation budget to vegetation management initiatives, including remediation of at-risk species 
(16 percent) and fuel management work (8 percent).

Liberty’s planned spend per HFTD circuit-mile at $63,000 is at the low end of the Small Multi-Jurisdictional Utilities (SMJUs) and is approximately 5 percent of Bear Valley Electric Service’s planned spend per HFTD circuit-mile.

Liberty is engaged in a multi-jurisdictional Forest Resiliency Corridor Project, with wider clearances (up to 175 feet on each side of lines in Zone 2, and 
1,000 feet on each side of lines) in Zone 3.

Deficiencies and Conditions - Vegetation management and inspections

Liberty provides inconsistent data regarding the number of overhead miles in HFTD Tier 3.

Data inconsistency is not unique to Liberty. As such, this deficiency and associated condition are addressed in the Guidance Resolution, WSD-001

Deficiency (LIB-2, Class B): Liberty reports inspection frequencies that raise concerns about effectiveness. Liberty is only planning for annual inspections in Tier 3, and a three-year cycle for other areas. This has proven to be inadequate to address grow-ins and fall-ins and has led to numerous instances of Public Resources Code (PRC) violations being identified. Similarly, Liberty’s third-party contractor reviews the inspection process every three years.  This appears to be too long of a delay to identify deficiencies in the program which may impact ignition potential.

Condition (LIB-2, Class B): In its first quarterly report, Liberty shall:

- justify its three-year cycle;

- report how it is meeting its PRC clearance requirements; and

- if its current inspection cycle is insufficient to avoid violations of clearance requirements, explain how they will resolve those deficiencies, including potential increases in frequency of inspections, reviews and audits.

Grid Operations and Operating Protocols

The grid operations and operating protocols section of the WMP requires discussion of ways the filer operates its system to reduce wildfire risk.  For example, disabling the reclosing function of automatic reclosers during periods of high fire danger (e.g., during Red Flag Warning conditions) can reduce utility ignition potential by minimizing the duration and amount of energy released when there is a fault.  This section also requires discussion of work procedures in elevated fire risk conditions, PSPS events and protocols, and whether the filer has stationed and on-call ignition prevention and suppression resources and services.

Liberty’s grid operation plans and operating protocols consist largely of a continuing effort to replace older reclosers and line air switches with newer equipment.  Its goals are to allow for better sectionalizing of circuits in PSPS events and to enable Distribution Automation Control in the next three years. Liberty’s projected $1.2 million budget for recloser replacements is mostly scheduled for 2021. The utility projects installing 4 reclosers per year.

Otherwise, Liberty points to other areas, including grid hardening and improved weather monitoring to support its operations and wildfire preparedness. Liberty’s elevated fire risk procedures are overseen by a Fire Safety Leader to assess risk, identify areas to be extinguished and deploying resources.  The work will be guided through the use of a wind/weather forecast tool referenced in the Situational Awareness section.

Appendix B, Figure 1.5b shows Liberty’s total annual RFW circuit mile days for each reporting year. This figure is leveraged as a proxy for differentiating fire weather potential (as a function of RFWs) year over year for each IOU. The figure in Appendix B, Figure 2.8b displays annual customer hours of PSPS events normalized across the WMP-defined metric of RFW circuit mile days. The intent of this normalizing metric is to account for varying fire weather conditions using a common metric of RFWs.

As shown in Appendix B, Figure 2.9b, Liberty reports its highest acreage burned rate and total acres burned in 2016. Interestingly, Appendix B, Figure 1.5b illustrates that in 2016 Liberty experienced its least amount of RFW circuit mile days in the past five years, indicating there may not be a strong correlation between these two metrics in Liberty’s service territory.

Liberty’s reported statistics for red flag warning circuit mile days are low, even when compared to other SMJUs, and varies with no clear trend.

Deficiencies and Conditions - Grid operations and operating protocols

Deficiency (LIB-3, Class C): Liberty’s WMP does not report detailed information about how its grid operations will reduce wildfire risk.

Liberty does not articulate how it plans to evolve grid operations to drive reduction in wildfire risk.  While installation of additional automated SCADA and improvements in weather forecasting are positive, Liberty is not demonstrating enough forward progress.

Condition (LIB-3, Class C): In its 2021 WMP update, Liberty shall:

- identify a more ambitious growth path for maturing grid operations that may serve as preventative mitigations against wildfires to drive reduction in wildfire risk.

Data Governance

The data governance section of the WMP Guidelines seeks information on the filer's initiatives to create a centralized wildfire-related data repository, conduct collaborative research on utility ignition and wildfire, document and share wildfire-related data and algorithms, and track and analyze near miss data.

Liberty’s data governance plans consist of a very limited platform for storage and utilization of data. A SharePoint platform is expected to be in use by this upcoming fire season, and it will be managed and refined over time.

One of Liberty’s stronger initiatives is their proposed collaboration with University of Nevada Reno to study high impedance faults in its service territory, as well as its planned deployment of Distribution Fault Anticipation on 10 distribution feeders in Tier 2 and Tier 3 zones.

Liberty’s goals are appropriate and achievable but are focused mainly on completing and maintaining current projects.

Resource Allocation Methodology

The resource allocation section of the WMPs requires the filer to describe its methodology for prioritizing programs to minimize the risk of its equipment or facilities causing wildfires in the most cost-efficient manner.  This section requires filers to discuss risk reduction scenario analysis and provide a RSE analysis for each aspect of the plan.

Liberty has not developed a resource allocation or risk assessment methodology other than its Enterprise Risk Management practices. Their view is looking at risk as an aggregate rather than looking on a mitigation by mitigation basis.  Currently, probability and consequence modeling, quantitative analysis, and metrics are not used by the utility to determine its risk reduction.

Liberty intends to develop a more relevant resource allocation methodology, incorporating current aspects of RAMP/S-MAP methodologies, for its 2021 GRC.  They are developing a risk-based decision making (RBDM) framework which will be integrating weather data from its own weather station system data and consequences for utility-caused fires ignitions, which should provide a modeling approach to evaluate wildfire risks in the future.

Appendix B, Figure 3.1b shows Liberty’s total planned spend during the plan period (2020-2022) is estimated to be $88 million. This represents a significant increase from the $7 million spent on similar activities in 2019.

While generally evenly dispersed in each year, averaging $29.3 million per year, Liberty projects $32 million in 2021, dropping to $27 million in 2022. The difference appears to be related to a $6 million undergrounding project.

Deficiencies and Conditions - Resource allocation methodology

Liberty has also not yet applied RSE to its decision making process, making it difficult to assess the expected cost-effectiveness of wildfire mitigations.

Deficiencies such as these are not unique to Liberty. As such, this deficiency and associated condition is addressed in the Guidance Resolution, WSD-002.

Emergency Planning and Preparedness

The WMP Guidelines require a general description of the filer's overall emergency preparedness and response plan, including discussion of how the plan is consistent with legal requirements for customer support before, during and after a wildfire, including support for low income customers, billing adjustments, deposit waivers, extended payment plan, suspension of disconnection and nonpayment fees, and repairs.  Filers are also required to describe emergency communications before, during, and after a wildfire in English, Spanish, and other languages required by the Commission

The WMP Guidelines also require discussion of the filer's plans for coordination with first responders and other public safety organizations, plans to prepare for and restore service, including workforce mobilization and prepositioning of equipment and employees, and a showing that the filer has an adequate and trained workforce to promptly restore service after a major event.

Liberty’s emergency planning and preparedness plans consist of compliance with Public Utilities Code sections 768.6 and 8386 requirements for emergency preparedness and response plans. The description of its program appears adequate to meet these standards, although the utility acknowledges challenges in recruiting and retaining adequate staff.  With regard to staffing for service restoration, Liberty’s WMP identified the need to hire a Fire Prevention Coordinator and a Fire Operations Specialist.

Deficiencies and Conditions - Emergency planning and preparedness

One area of concern is Liberty’s relatively small workforce. Currently, it is addressing limitations via mutual aid agreements with other utilities and organizations. The plan does not address a circumstance in which a region-wide emergency might limit the ability of mutual aid partners to respond to requests for assistance.

Deficiencies such as these are not unique to Liberty.  As such, this deficiency and associated condition is addressed in the Guidance Resolution, WSD-002.

Deficiency (LIB-4, Class B): Liberty notes the challenge of attracting and retaining employees in the high-cost Lake Tahoe community.

Liberty identifies the high cost of living in its service territory as a potential labor challenge for WMP implementation but provides no discussion regarding its plans or strategy for labor recruitment.

Condition (LIB-4, Class B): In its first quarterly report, Liberty shall detail:

- its recruitment and retention strategy for labor, considering the high cost of living in its service territory, and

- how it plans to deal with this constraining factor in scaling its WMP programs and initiatives.

Stakeholder Cooperation and Community Engagement

The final topic covered in Section 5 relates to the extent to which the filer will engage the communities it serves and cooperate and share best practices with community members, agencies outside California, fire suppression agencies, forest service entities and others engaged in vegetation management or fuel reduction.

Liberty’s stakeholder cooperation and community engagement is nascent, with little or no activity reported to date but expectations for improvement. In 2020, it plans to commence a two-phased stakeholder engagement process: continuing an Expert Working Group engagement to inform the next WMP; and Public Outreach for Plan Review. The latter will involve community workshops in 
10 identified locations (with others to be determined). The WMP proposes a $75,000 budget for these activities in 2020, and no other years.

Liberty’s protocols for PSPS notification and service restoration comply with recently revised Commission rules and guidance decisions.

Maturity Evaluation

In 2020, the WSD introduced a new Utility Wildfire Mitigation Maturity Model, to establish a baseline understanding of utilities’ current and projected capabilities and assess whether each utility is progressing sufficiently to improve its ability to mitigate wildfire risk effectively.  The maturity model also serves as an objective means of comparing across utilities and provides a framework for driving utility progress in wildfire risk mitigation over time.  WMP filers were required to complete a survey in which they answered specific questions which assessed their existing and future wildfire mitigation practices across 52 capabilities at the time of filing and at the end of the 3-year plan horizon.  The 
52 capabilities are mapped to the same 10 categories identified in Section 5 above.

The maturity model will continue to evolve each year to reflect best practices and lessons learned.  With the inaugural use of the maturity model in 2020, it is important to note that the resulting maturity score is to be informative of a utility’s capabilities within the context of the underlying assessment criteria.  Accordingly, it is essential that the maturity assessment scores are understood within the context of the qualitative detail supporting each score.  The model results require context and should not be interpreted as the final word on an electrical corporation’s wildfire mitigation capabilities without an understanding of the scoring process described in the Guidance Resolution. As such, the final maturity model outputs should be viewed as levels or thresholds – they are not absolute scores.

Liberty’s initial maturity model assessment reveals that it is in the early stages of its maturity in most areas and is focused on building foundational capabilities for (G.) data governance and developing its (H.) resource allocation methodologies.  The maturity model results give somewhat less attention to advancing its current capabilities for (A.) risk assessment & mapping, (B.) situational awareness, and (F.) grid operations capabilities.

Liberty’s development in these foundational, enabling capabilities provides an opportunity for the WSD and the Commission to guide this development and drive towards increased transparency and standardization in decision-making. As shown in Section 1.3 of Appendix C, Liberty generally projects growth across all 10 categories between 2020 and 2023.

Admittedly at or near the starting point for developing the majority of capabilities (44 out of 52), Liberty appears to be strategically focused on achieving stronger than incremental improvements in about half of the identified areas between 2020 and 2023.

As mentioned, data governance activities are a strong area of attention, and Liberty intends to substantially improve all four capabilities: data collection and curation, data transparency and analytics, near miss tracking, and data sharing with the research community.  By 2023, Liberty expects to be at or near the top level for all these capabilities.

Not quite so ambitious growth is projected for each of the six areas associated with improving (H.) resource allocation methodology. But Liberty is targeting better than incremental maturation of scenario analysis, use of RSE for determining mitigations related to vegetation management and system hardening, and portfolio-wide innovations in new wildfire mitigations.

Liberty’s efforts in the C.) grid design and system hardening category appear to be focused on cost efficiency and grid design and innovation.  However, its activities related to (E.) vegetation management are largely static over the three-year period.  While it intends to build upon current inventory for condition assessment capabilities, and improve Quality Assurance/Quality Control of its VM programs, Liberty is holding steady on other aspects, such as inspection cycles and effectiveness,  and mitigations to limit fall-in and grow-in contacts.

Other areas where Liberty is putting an effort on substantively maturing its operations include:  Asset maintenance and repair, ignition prevention and wildfire detection.  Surprisingly, however, it does not project much if any advancement of its other risk assessment & mapping or situational awareness capabilities.

With regard to (I.) emergency planning and preparedness, Liberty’s priority appears to be greatly improving its protocols to learn from wildfire events.  It projects general improvement to (J.) stakeholder co-operation and community engagement, although no growth is projected for community engagement in developing mitigation initiatives or advancing collaboration for mitigation planning.

It intends to achieve better than incremental growth for most of its targeted capabilities.  It would be expected that the results of these efforts will result in re-prioritization in the future.

Impact of COVID-19 Pandemic

After Liberty submitted its WMP, on March 19, 2020, California Governor Gavin Newsom signed Executive Order N-33-20 requiring Californians to stay at home to combat the spread of the COVID-19 virus.  Specifically, Governor Newsom required Californians to heed the order of the California State Public Health Officer and the Director of the California Department of Public Health that all individuals living in California stay home or at their place of residence, except as needed to maintain continuity of operation of the federal critical infrastructure sectors, in order to address the public health emergency presented by the COVID-19 disease (stay-at-home order).

As articulated in the March 27, 2020, joint letters of the WSD, CAL FIRE and the California Governor’s Office of Emergency Services regarding essential wildfire and PSPS mitigation work during COVID-19 sent to each electrical corporation, electrical corporations are expected to continue to prioritize essential safety work. The WSD expects the electrical corporations to make every effort to keep WMP implementation progress on track, including necessary coordination with local jurisdictions.  Such effort is essential to ensuring that electrical corporations are prepared for the upcoming and subsequent wildfire seasons, while complying with COVID-19 restrictions requiring residents to shelter-in-place, practice social distancing, and comply with other measures that California’s public health officials may recommend or that Governor Newsom or other officials may require in response to the COVID-19 pandemic.

Furthermore, the WSD expects the electrical corporations to continue to make meaningful progress on PSPS mitigation goals, including continuing with sectionalization projects, local outreach and coordination, establishing customer resource centers, and microgrid projects. Electrical corporations are expected to limit planned outage work during this time to wildfire mitigation, PSPS reduction, projects that immediately impact reliability if delayed, and emergency/public safety outages. In addition, electrical corporations are expected to undertake any other critical work related to operating a safe and reliable grid and to mitigate wildfire and/or PSPS risk.

Conclusion

- Liberty’s Wildfire Mitigation Plan contains all of the elements required by AB 1054, Pub. Util. Code Section 8386(c) and all the elements required by the WMP Guidelines.

- Liberty’s WMP is approved by the WSD, subject to the conditions set forth in Appendix A.

Comments

Pub. Util. Code § 311(g)(1) provides that resolutions must be served on all parties and subject to at least 30 days public review. However, given that this resolution is issued outside of a formal proceeding, interested stakeholders need not have party status in R.18-10-007 in order to submit comments on the resolution. Please note that comments are due 20 days from the mailing date of this resolution. Replies will not be accepted.

This draft resolution was served on the service list of R.18-10-007 and posted on the Commission’s website, www.cpuc.ca.gov/wildfiremitigationplans, and it will be placed on the Commission's agenda no earlier than 30 days from today.

Findings

- AB 1054 and Commission Resolution WSD-001 require Liberty to file a WMP for 2020 that conforms with Pub. Util. Code § 8386(c) and guidance provided by the WSD and served on the R.18-10-007 service list on December 16, 2019 by ALJ ruling.

- The WMPs were reviewed and acted upon with due consideration given to comments received from governmental agencies, the WSAB, members of the public, and all other relevant stakeholders.

- The WMPs were reviewed and acted upon in compliance with all relevant requirements of state law.

- Liberty’s WMP contains all of the elements required by AB 1054, Pub. Util. Code § 8386(c).

- Liberty has satisfied the requirements of Pub. Util. Code § 8386(c) and the WMP Guidelines.

- Appendix A contains findings regarding deficiencies in Liberty’s WMP.

THEREFORE, IT IS ORDERED THAT:

- Ratification of the Wildfire Safety Division’s approval of Liberty Utility/CalPeco Electric’s Wildfire Mitigation Plan is subject to conditions set forth in Appendix A.

- The Wildfire Safety Division’s approval of Liberty Utility/CalPeco Electric’s 2020 Wildfire Mitigation Plan, conditioned upon Liberty’s compliance with the conditions listed in Appendix A, is hereby ratified.

- Liberty Utilities/CalPeco Electric shall submit an update to its Wildfire Mitigation Plan in 2021 according to the forthcoming guidance and schedule issued by the Wildfire Safety Division.

- Liberty Utilities/CalPeco Electric shall submit a new comprehensive 3-year Wildfire Mitigation Plan in 2023.

- Nothing in this Resolution should be construed as approval of the costs associated with Liberty Utility/CalPeco Electric’s Wildfire Mitigation Plan mitigation efforts.

- Liberty Utilities/CalPeco Electric may track the costs associated with its Wildfire Mitigation Plan in a memorandum account, by category of costs, and shall be prepared for Commission review and audit of the accounts at any time.

- Liberty Utilities/CalPeco Electric shall submit a letter to the Wildfire Safety Division containing any updates to scope, timing or other aspects of any mitigation set forth in its Wildfire Mitigation Plan as result of the COVID-19 pandemic, including Public Safety Power Shutoff. The letter shall list items using the same names and sections used in the Wildfire Mitigation Plan and give a thorough description of why the COVID-19 pandemic requires the specified action. The letter shall be submitted within 60 days of issuance of this Resolution and shall be addressed to the Director of the Wildfire Safety Division. The letter shall be emailed to wildfiresafetydivision@cpuc.ca.gov with service on the service list of Rulemaking 18-10-007.  If there are no changes to report, no such submission is required.

- Nothing in this Resolution should be construed as a defense to any enforcement action for a violation of a Commission decision, order, or rule.

This Resolution is effective today.

I certify that the foregoing resolution was duly introduced, passed and adopted at a conference of the Public Utilities Commission of the State of California held on ________________; the following Commissioners voting favorably thereon:

______________________

Alice Stebbins
Executive Director

BEFORE THE PUBLIC UTILITIES COMMISSION OF THE STATE OF CALIFORNIA

RESOLUTION WSD-007 Resolution Ratifying Action of the Wildfire Safety Division on PacifiCorp’s 2020 Wildfire Mitigation Plan Pursuant to Public Utilities Code Section 8386.

INFORMATION REGARDING SERVICE

I have electronically served all persons on the attached official service list who have provided an e-mail address for R.18-10-007.

Upon confirmation of this document’s acceptance for filing, I will cause a Notice of Availability of the document to be served by U.S. mail on all parties listed in the “Party” category of the official service list for whom no e-mail address is provided.

The official service list I use is current as of today’s date.

Dated May 7, 2020, at San Francisco, California.

/s/ MARILOU HIPOLITO

Marilou Hipolito

NOTICE

Persons should notify the Process Office, Public Utilities Commission, 505 Van Ness Avenue, Room 2000, San Francisco, CA  94102, of any change of address to ensure that they continue to receive documents.  You must indicate the proceeding number on the service list on which your name appears.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The Commission’s policy is to schedule hearings (meetings, workshops, etc.) in locations that are accessible to people with disabilities.  To verify that a particular location is accessible, call: Calendar Clerk (415) 703-1203.

If specialized accommodations for the disabled are needed, e.g., sign language interpreters, those making the arrangements must call the Public Advisor at (415) 703-2074 or TDD# (415) 703-2032 five working days in advance of the event.

| ************** PARTIES ************** William B. Abrams Community Advocate 1519 BRANCH OWL PLACE SANTA ROSA CA 95409 (707) 787-7759 End2EndConsulting@gmail.com For: William B. Abrams ____________________________________________ Rachael E. Koss Attorney ADAMS BROADWELL JOSEPH & CARDOZO 601 GATEWAY BLVD., SUITE 1000 SOUTH SAN FRANCISCO CA 94080 (650) 589-1660 X13 RKoss@AdamsBroadwell.com For: Coalition of California Utility Employees (CUE) ____________________________________________ Michael J. Agurre, Esq. AGUIRRE & SEVERSON LLP 501 WEST BROADWAY, SUITE 1050 SAN DIEGO CA 92101 (619) 876-5364 maguirre@amslawyers.com For: Ruth Henricks ____________________________________________ Valerie Pryor Gen. Mgr. ALAMEDA COUNTY FLOOD CONTROL AND WATER 100 NORTH CANYONS PARKWAY LIVERMORE CA 94551 (925) 454-5000 vpryor@zone7water.com For: Alameda County Flood Control and Water Conservation District, Zone 7 ____________________________________________ David J. Miller Avp - Sr. Legal Counsel AT&T SERVICES, INC. 430 BUSH STREET, 6TH FL. SAN FRANCISCO CA 94108 (415) 268-9497 DavidJMiller@att.com For: AT&T ____________________________________________ | Keith Switzer BEAR VALLEY ELECTRIC SERVICE 630 EAST FOOTHILL BLVD. SAN DIMAS CA 91773 (909) 394-3600 X-759 kswitzer@gswater.com For: Bear Valley Electric Service, div of Golden State Water Company ____________________________________________ Christi Hogin Counsel BEST BEST & KRIEGER LLP 1230 ROSECRANS AVE., STE. 110 MANHATTAN BEACH CA 90266 (310) 643-8448 Christi.Hogin@bbkLaw.com For: City of Malibu ____________________________________________ Douglas E. Coty Attorney BOLD, POLISNER, MADDOW, NELSON & JUDSON 2125 OAK GROVE ROAD, SUITE 210 WALNUT CREEK CA 94598 (925) 933-7777 DCoty@bpmnj.com For: Contra Costa Water District ____________________________________________ Justin Wynne Attorney BRAUN BLAISING SMITH WYNNE, P.C. 915 L STREET, STE. 1480 SACRAMENTO CA 95814 (916) 326-5813 Wynne@BraunLegal.com For: California Municipal Utilities Association (CMUA) ____________________________________________ Evelyn Kahl Attorney BUCHALTER, A PROFESSIONAL CORPORATION 55 SECOND STREET, SUITE 1700 SAN FRANCISCO CA 94105-3493 (415) 227-3563 EKahl@Buchalter.com For: Energy Producers and Users Coalition ____________________________________________ Michael Alcantar Attorney At Law BUCHALTER, A PROFESSIONAL CORPORATION 55 SECOND STREET, SUITE 1700 SAN FRANCISCO CA 94105 (415) 227-0900 MAlcantar@Buchalter.com For: Western States Petroleum Association ____________________________________________ |
| --- | --- |
| Nora Sheriff, Esq. Counsel BUCHALTER, A PROFESSIONAL CORPORATION 55 SECOND STREET, STE. 1700 SAN FRANCISCO CA 94105 (415) 227-3551 NSheriff@Buchalter.com For: California Large Energy Consumers Association (CLECA) ____________________________________________ Jerome F. Candelaria Vp & Counsel, Regulatory Affairs CALIFORNIA CABLE AND TELECOMM. ASSN. 1001 K STREET, 2ND FL. SACRAMENTO CA 95814-3832 (916) 446-7732 Jerome@CalCable.org For: California Cable and Telecommunications Association ____________________________________________ Karen Noreen Mills Sr. Attorney CALIFORNIA FARM BUREAU FEDERATION 2600 RIVER PLAZA DRIVE SACRAMENTO CA 95833 (916) 561-5655 KMills@CFBF.com For: California Farm Bureau Federation ____________________________________________ John Larrea Dir - Govn'T Affairs CALIFORNIA LEAGUE OF FOOD PRODUCERS 2485 NATOMAS PARK DRIVE, STE. 550 SACRAMENTO CA 95833 (916) 640-8150 John@clfp.com For: California League of Food Producers ____________________________________________ Peter Smith CITIZENS TRANSMISSION LLC 88 BLACK FALCON AVENUE, SUITE 342 BOSTON MA 02210 Peter_Smith@CitizensEnergy.com For: Citizens Transmission LLC ____________________________________________ William Rostov Deputy City Attorney CITY AND COUNTY OF SAN FRANCISCO CITY HALL 1 DR CARLTON B. GOODLET PL. RM 234 SAN FRANCISCO CA 94102-4682 (415) 554-4700 William.Rostov@SFcityAtty.org For: City and County of San Francsico ____________________________________________ | Luisa F. Elkins Sr. Deputy City Attorney CITY OF SAN JOSE 200 EAST SANTA CLARA ST., 16TH FL TOWER SAN JOSE CA 95113-1905 (408) 535-1953 Luisa.Elkins@SanJoseCa.gov For: City of San JosÃ© ____________________________________________ Shana Lazerow Attorney COMMUNITIES FOR A BETTER ENVIRONMENT 120 BROADWAY, SUITE 2 RICHMOND CA 94804 (510) 302-0430 X18 SLazerow@cbecal.org For: California Environmental Justice Alliance (CEJA) ____________________________________________ Kelley Williams COUNTY OF INYO PO DRAWER N INDEPENDENCE CA 93526 (760) 878-0120 KWilliams@inyoCounty.us For: County of Inyo ____________________________________________ J. Scott Kuhn COUNTY OF LOS ANGELES OFFICE OF THE COUNTY COUNSEL 500 WEST TEMPLE STREET, STE 652 LOS ANGELES CA 90012-2713 (213) 974-1852 SKuhn@Counsel.LAcounty.gov For: County of Los Angeles ____________________________________________ Tiffany M. Lin Deputy County Counsel COUNTY OF SANTA CLARA 70 W. HEDDING ST., EAST WING, 9TH FL. SAN JOSE CA 95110 (408) 299-5900 Tiffany.M.Lin@CCO.SCCgov.org For: County of Santa Clara ____________________________________________ Jason Hoppin COUNTY OF SANTA CRUZ ADMIN. OFFICE 701 OCEAN STREET SANTA CRUZ CA 95060 (831) 454-2100 Jason.Hoppin@SantaCruzCounty.us For: County of Santa Cruz ____________________________________________ |
| Christopher Clay Legal Division RM. 4300 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1123 cec@cpuc.ca.gov For: Office of The Safety Advocate (OSA) Jedediah J. Gibson Attorney ELLISON SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVENUE, SUITE 400 SACRAMENTO CA 95816-5931 (916) 447-2166 JJG@ESlawFirm.com For: Bear Valley Electric Service (BVES) / Liberty Utilities (CalPeco Electric) ____________________________________________ Lynn Haug Attorney ELLISON SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVE., STE. 400 SACRAMENTO CA 95816 (916) 447-2166 LMH@ESLawFirm.com For: East Bay Municipal Utility District ____________________________________________ Ronald Liebert Attorney At Law ELLISON SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVENUE, STE. 400 SACRAMENTO CA 95816 (916) 447-2166 RL@eslawfirm.com For: California Manufacturers & Technology Assn. (CMTA) ____________________________________________ Megan Somogyi Attorney GOODIN, MACBRIDE, SQUERI & DAY, LLP 505 SANSOME STREET, STE 900 SAN FRANCISCO CA 94111 (415) 392-7900 MSomogyi@GoodinMacBride.com For: City of Santa Rosa ____________________________________________ Megan Somogyi Attorney GOODIN, MACBRIDE, SQUERI & DAY, LLP 505 SANSOME STREET, STE. 900 SAN FRANCISCO CA 94111 (415) 392-7900 MSomogyi@GoodinMacBride.com For: City of Placerville ____________________________________________ | Megan Somogyi Attorney GOODIN, MACBRIDE, SQUERI & DAY, LLP 505 SANSOME STREET, STE. 900 SAN FRANCISCO CA 94111 (415) 392-7900 MSomogyi@GoodinMacBride.com For: County of Mendocino ____________________________________________ Megan Somogyi Attorney GOODIN, MACBRIDE, SQUERI, & DAY, LLP 505 SANSOME ST., STE. 900 SAN FRANCISCO CA 94111 (415) 392-7900 MSomogyi@GoodinMacBride.com For: County of Sonoma ____________________________________________ Charlyn A. Hook Legal Division RM. 5123 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3050 chh@cpuc.ca.gov For: Public Advocates Office Tim Lindl Partner KEYES & FOX LLP 436 14TH STREET, SUITE 1305 OAKLAND CA 94612 (510) 314-8385 TLindl@KeyesFox.com For: Sunrun Inc. ____________________________________________ Irene K. Moosen Attorney At Law LAW OFFICE OF IRENE K. MOOSEN 53 SANTA YNEZ STREET SAN FRANCISCO CA 94112 (415) 587-7343 Irene@igc.org For: Local Government Sustainable Energy Coalition (LGSEC) ____________________________________________ Daniel Marsh Mgr - Rates & Regulatory Affairs LIBERTY UTILITIES (CALPECO ELECTRIC) LLC 933 ELOISE AVENUE SOUTH LAKE TAHOE CA 96150 (562) 299-5104 Dan.Marsh@LibertyUtilities.com For: Liberty Utilities (CalPecoElectric) ____________________________________________ |
| David L. Huard Attorney MANATT, PHELPS & PHILLIPS, LLP ONE EMBARCADERO CENTER, 30TH FL. SAN FRANCISCO CA 94111-3736 (415) 291-7430 DHuard@manatt.com28 For: City of Laguna Beach ____________________________________________ Diane Conklin Spokesperson MUSSEY GRADE ROAD ALLIANCE PO BOX 683 RAMONA CA 92065 (760) 787-0794 dj0Conklin@Earthlink.net For: Mussey Grade Road Alliance ____________________________________________ Jeffery Richard Chief Deputy County Counsel OFFICE OF THE NAPA COUNTY COUNSEL 1195 THIRD ST, SUITE 301 NAPA CA 94559 (707) 253-4234 Jeffery.Richard@CountyOfNapa.org For: County of Napa ____________________________________________ Alyssa Koo Attorney PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B30A SAN FRANCISCO CA 94105 (415) 973-3386 ATK4@pge.com For: Pacific Gas and Electric Company (PG&E) ____________________________________________ Cynthia Hansen Mifsud Assist. Gen. Counsel PACIFICORP 825 NE MULTNOMAH ST., STE. 1800 PORTLAND OR 97232 (503) 813-6566 Cynthia.Hansen@PacifiCorp.com For: Pacific Power, a div of PacifiCorp ____________________________________________ | Malinda Dickenson General Counsel PROTECT OUR COMMUNITIES FOUNDATION 4452 PARK BLVD., STE 202 SAN DIEGO CA 92116 (858) 521-8492 Malinda@ProtectOurCommunities.org For: Protect Our Communities Foundation ____________________________________________ Staci Heaton Regulatory Affairs Advocate RURAL COUNTY REPRESENTATIVES OF CALIF. 1215 K ST., STE. 1650 SACRAMENTO CA 95814 (916) 447-4806 SHeaton@RCRCnet.org For: Rural County Representatives of California ____________________________________________ Kirstie C. Raagas Regulatory Counsel SAN DIEGO GAS & ELECTRIC COMPANY 8330 CENTURY PARK COURT, CP32F SAN DIEGO CA 92123 (619) 699-5003 KRaagas@SempraUtilities.com For: San Diego Gas & Electric Company ____________________________________________ Matthew J. Sanders Deputy County Counsel SAN MATEO COUNTY COUNSELâ€™S OFFICE 400 COUNTY CENTER, 6TH FL REDWOOD CITY CA 94063 (650) 363-4461 MJSanders@SMCgov.org For: Peninsula Clean Energy Authority ____________________________________________ James M. Birkelund President SMALL BUSINESS UTILITY ADVOCATES 548 MARKET STREET, STE. 11200 SAN FRANCISCO CA 94104 (415) 602-6223 James@UtilityAdvocates.org For: Small Business Utility Advocates (SBUA) ____________________________________________ |
| Russell A. Archer Sr. Attorney SOUTHERN CALIFORNIA EDISON COMPANY 2244 WALNUT GROVE AVE. / PO BOX 800 ROSEMEAD CA 91770 (626) 302-2865 Russell.Archer@SCE.com For: Southern California Edison Company ____________________________________________ Ali Amirali STARTRANS IO, LLC 591 W. PUTNAM AVENUE GREENWICH CT 06830 AAmirali@Starwood.com For: Startrans IO, LLC ____________________________________________ Alan Stein Impacted Individual 14301 HANSON CIRCLE MENDOCINO CA 95460 (707) 964-6514 bugadi@comcast.net For: Alan Stein ____________________________________________ Gregg Morris Director THE GREEN POWER INSTITUTE 2039 SHATTUCK AVE., SUTE. 402 BERKELEY CA 94704 (510) 644-2700 GMorris@emf.net For: The Green Power Institute (GPI) ____________________________________________ Thomas Long Legal Director THE UTILITY REFORM NETWORK 785 MARKET ST., STE. 1400 SAN FRANCISCO CA 94103 (415) 929-8876 X-303 TLong@turn.org For: TURN ____________________________________________ Lauren Gill Town Mgr. TOWN OF PARADISE 5555 SKYWAY PARADISE CA 95969 (530) 872-6291 LGill@TownOfParadise.com For: Town of Paradise ____________________________________________ | Lenneal K. Gardner Principal Attorney TRANS BAY CABLE LLC ONE LETTERMAN DRIVE, C5-100 SAN FRANCISCO CA 94129 (415) 291-2300 Lenneal.Gardner@TransBayCable.com For: Trans Bay Cable LLC ____________________________________________ Robert L. Mitchell TRANS-ELECT NTD PATH 15, LLC 1850 CENTENNIAL PARK DRIVE, SUITE 480 RESTON VA 20191 RLMitchell@Trans-Elect.com For: Trans-Elect NTD Path 15, LLC ____________________________________________ Lisa A. Cottle Attorney / Partner WINSTON & STRAWN LLP 101 CALIFORNIA STREET, 34TH FL. SAN FRANCISCO CA 94111 (415) 591-1579 LCottle@Winston.com For: Horizon West Transmission, LLC (formerly NextEra Energy Transmission West, LLC - NEET West) ____________________________________________ Hans Laetz General Mgr. ZUMA BEACH FM BROADCASTERS RADIO MALIBU 99.1 FM KBUU 6402 SURFSIDE WAY MALIBU CA 90265 (424) 442-9862 HansLaetz@gmail.com For: Zuma Beach FM Emergency and Community Broadcasters, Inc. ____________________________________________ ********** STATE EMPLOYEE *********** ********* INFORMATION ONLY ********** Andrew J. Graf Associate Attorney ADAMS BROADWELL JOSEPH & CARDOZO 601 GATEWAY BOULEVARD, SUITE 1000 SOUTH SAN FRANCISCO CA 94080 (650) 589-1660 X16 AGraf@AdamsBroadwell.com |
| Marc D. Joseph Attorney At Law ADAMS BROADWELL JOSEPH & CARDOZO 601 GATEWAY BLVD., STE. 1000 SOUTH SAN FRANCISCO CA 94080 (650) 589-1660 MDJoseph@AdamsBroadwell.com Miles F. Maurino ADAMS BROADWELL JOSEPH & CARDOZO 601 GATEWAY BLVD., SUITE 1000 SOUTH SAN FRANCISCO CA 94080 (650) 589-1660 MMaurino@AdamsBroadwell.com For: Coalition of California Utility Employees (CUE) ____________________________________________ Maria Byrnes Legal Assistant AGUIRRE & SEVERSON LLP 501 WEST BROADWAY, STE. 1050 SAN DIEGO CA 92101 (619) 876-5364 MByrnes@amslawyers.com For: Ruth Henricks ____________________________________________ Maria C. Severson, Esq. Attorney AGUIRRE & SEVERSON LLP 501 WEST BROADWAY, STE. 1050 SAN DIEGO CA 92101-3591 (619) 876-5364 MSeverson@amslawyers.com For: Ruth Henricks ____________________________________________ Ashley Vinson Crawford AKIN GUMP STRAUSS HAUER & FELD LLP 580 CALIFORNIA ST, SUITE 1500 SAN FRANCISCO CA 94104 (415) 765-9561 AVCrawford@AkinGump.com For: Ad Hoc Committee of Senior Unsecured Noteholders of Pacific Gas and Electric Company ____________________________________________ George D.(Chip) Cannon, Jr. AKIN GUMP STRAUSS HAUER & FELD LLP 580 CALIFORNIA STREET, STE. 1500 SAN FRANCISCO CA 94104 (415) 765-9500 CCannon@AkinGump.com For: Ad Hoc Committee of Senior Unsecured Noteholders of Pacific Gas and Electric Company ____________________________________________ | J. Porter Wiseman AKIN GUMP STRAUSS HAUER & FELD LLP 2001 K STREET N.W. WASHINGTON DC 20006 (202) 887-4219 JWiseman@AkinGump.com For: Ad Hoc Committee of Senior Unsecured Noteholders of Pacific Gas and Electric Company ____________________________________________ Andy Umana Senior Paralegal AT&T SERVICE 430 BUSH STREET, ROOM 6043 SAN FRANCISCO CA 94108 (415) 268-5304 andy.umana@att.com Fassil Fenikile Dir - Regulatory AT&T SERVICES, INC. 430 BUSH STREET, 5TH FL. SAN FRANCISCO CA 94108 (415) 417-5020 Fassil.T.Fenikile@att.com Gwen Johnson Quality Testing AT&T SERVICES, INC. 430 BUSH STREET, 5TH FL. SAN FRANCISCO CA 94108 (415) 417-5034 Gwen.Johnson@att.com Jeffrey Mondon Dir - Regulatory AT&T SERVICES, INC. 430 BUSH STREET, 5TH FL SAN FRANCISCO CA 94108 (415) 417-5021 jeffrey.mondon@att.com Michelle Choo Assistant AT&T SERVICES, INC. 430 BUSH STREET, 3ND FL. SAN FRANCISCO CA 94108 (415) 268-9494 michelle.choo@att.com Sultan Banu Acimis Safety and Enforcement Division 180 Promenade Circle, Suite 115 Sacramento CA 95834 2939 (916) 928-3826 sba@cpuc.ca.gov For: SED |
| Adenike Adeyeye Executive Division RM. 5214 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2005 ade@cpuc.ca.gov Wendy Al-Mukdad Safety Policy Division AREA 4-A 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2311 wmp@cpuc.ca.gov Catherine E. Yap BARKOVICH & YAP, INC. PO BOX 11031 OAKLAND CA 94611 (510) 450-1270 Cathy@BarkovichAndYap.com Paul Nelson Consultant BARKOVICH & YAP, INC. PO BOX 11031 OAKLAND CA 94611 (707) 937-6203 Paul@BarkovichAndYap.com Britt K. Strottman BARON & BUDD, P.C. 11440 WEST BERNARD COURT SAN DIEGO CA 92127 (415) 310-7523 BStrottman@BaronBudd.com For: Counties of Sonoma, Napa, Mendocino, Lake, Yuba, Nevada. Cities of Santa Rosa, and Clearlake. ____________________________________________ Kelcie Abraham BCG 2 EMBARCADERO CENTER SUITE 24 SF CA 94111 bcgpolicylists@bcg.com Eric Cardella Supervisor, Engineering & Planning BEAR VALLEY ELECTRIC SERVICE 42020 GARSTIN DRIVE / PO BOX 1547 BIG BEAR LAKE CA 92315 (909) 866-4678 X140 Eric.Cardella@bves.com | Marc Stern BEAR VALLEY ELECTRIC SERVICE 42020 GARSTIN DR./ PO BOX 1547 BIG BEAR LAKE CA 92315 (909) 866-4678 X151 marc.stern@bves.com Nguyen Quan Regulatory Affairs Mgr. BEAR VALLEY ELECTRIC SERVICE 630 EAST FOOTHILL BLVD. SAN DIMAS CA 91773 (909) 394-3600 X664 NQuan@GSwater.com Paul Marconi Director BEAR VALLEY ELECTRIC SERVICE 42020 GRASTIN DRIVE / PO BOX 1547 BIG BEAR LAKE CA 92315 (909) 202-9539 Paul.Marconi@bves.com Deborah Behles Of Counsel 2912 DIAMOND STREET, STE 162 SAN FRANCISCO CA 94131 (415) 841-3304 Deborah.Behles@gmail.com For: California Environmental Justice Alliance (CEJA) ____________________________________________ Benjamin Bodell Attorney BEST BEST AND KRIEGER LLP 2001 N MAIN ST., STE. 390 WALNUT CREEK CA 94596 (925) 977-3377 Benjamin.Bodell@bbklaw.com Joshua Nelson Attorney BEST BEST AND KRIEGER LLP 500 CAPITOL MALL, STE. 1700 SACRAMENTO CA 95814 (916) 551-2859 Joshua.Nelson@bbklaw.com Laura Fernandez Attorney BRAUN BLAISING SMITH WYNNE, P.C. 915 L STREET, STE 1480 SACRAMENTO CA 95814 (916) 326-5812 Fernandez@BraunLegal.com For: California Municipal Utilities Association ____________________________________________ |
| Kari Cameron Legal Administrator BUCHALTER EMAIL ONLY EMAIL ONLY CA 94105 (415) 227-3581 KCameron@Buchalter.com Gwenn O'Hara Attorney BUCHALTER, A PROFESSIONAL CORPORATION 500 CAPITOL MALL, SUITE 1900 SACRAMENTO CA 95814 (916) 945-5170 GOHara@Buchalter.com Lillian Rafii Attorney BUCHALTER, A PROFESSIONAL CORPORATION 55 SECOND STREET, STE. 1700 SAN FRANCISCO CA 94105-3493 (415) 227-3586 LRafii@Buchalter.com For: Energy Producers and Users Coalition ____________________________________________ Meghan Thomas, Esq. Associate BUCHALTER, A PROFESSIONAL CORPORATION 500 CAPITOL MALL, SUITE 1900 SACRAMENTO CA 95814 (916) 945-5176 MThomas@Buchalter.com Michael Cade Analyst - Energy & Nat'L Resources BUCHALTER, A PROFESSIONAL CORPORATION 55 SECOND STREET, SUITE 1700 SAN FRANCISCO CA 94105 (415) 227-3583 MCade@Buchalter.com Sarbjit Bagri Safety Policy Division 180 Promenade Circle, Suite 115 Sacramento CA 95834 2939 (916) 713-4143 sab@cpuc.ca.gov Andie Biggs Safety and Enforcement Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3305 ab6@cpuc.ca.gov | Billie C. Blanchard Energy Division AREA 4-A 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2068 bcb@cpuc.ca.gov Truman L. Burns Public Advocates Office RM. 4205 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2932 txb@cpuc.ca.gov Henry Burton Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-7311 hnb@cpuc.ca.gov Diane Fellman Vice Chair CA WILDFIRE SAFETY ADVISORY BOARD EMAIL ONLY EMAIL ONLY CA 00000 diane.fellman@cpuc.ca.gov Rachel A. Gold, Esq. Climate Chg Program CALIFORNIA AIR RESOURCES BOARD EMAIL ONLY EMAIL ONLY CA 00000 (916) 323-0560 rachel.gold@arb.ca.gov Benjamin Dawson CALIFORNIA COMMUNITY CHOICE ASSOCIATION EMAIL ONLY EMAIL ONLY CA 00000 regulatory@cal-cca.org For: CalCCA ____________________________________________ Kavya Balaraman Staff Writer / Reporter CALIFORNIA ENERGY MARKETS EMAIL ONLY EMAIL ONLY CA 00000 (415) 963-4439 X16 Kavya@NewsData.com |
| Mavis Scanlon Editor CALIFORNIA ENERGY MARKETS 425 DIVISADERO ST., STE 303 SAN FRANCISCO CA 94117 (415) 963-4439 X12 Mavis@NewsData.com Alex J. Morris Vp - Policy & Opers CALIFORNIA ENERGY STORAGE ALLIANCE 2150 ALLSTON WAY, STE.400 BERKELEY CA 94704 (510) 665-7811 X110 CESA_Regulatory@StorageAlliance.org Deborah Behles Of Counsel CALIFORNIA ENVIRONMENTAL JUSTICE ALLIANC 2912 DIAMOND STREET, NO. 160 SAN FRANCISCO CA 94131 (415) 841-3304 Deborah.Behles@gmail.com Jordan Pinjuv Sr. Counsel CALIFORNIA INDEPENDENT SYSTEM OPERATOR 250 OUTCROPPING WAY FOLSOM CA 95630 (916) 351-4429 JPinjuv@caiso.com For: California ISO ____________________________________________ Matthew Karle Public Advocates Office CALIFORNIA PUBLIC UTILITIES COMMISSION EMAIL ONLY EMAIL ONLY CA 00000 (415) 703-1850 mk3@cpuc.ca.gov Nick Cronenwett Legislative Analyst CALIFORNIA STATE ASSOC. OF COUNTIES 1100 K STREET, STE 101 SACRAMENTO CA 95814 (916) 650-8108 X531 NCronenwett@Counties.org | Tony Brunello CALIFORNIA STRATEGIES & ADVOCACY, LLC 1 EMBARCADERO CENTER, STE. 1060 SAN FRANCISCO CA 94111 (916) 718-8292 TBrunello@outlook.com Jennifer Capitolo Exe Dir CALIFORNIA WATER ASSOCIATION 601 VAN NESS AVENUE, STE. 2047 SAN FRANCISCO CA 94102-6316 (415) 561-9650 JCapitolo@CalWaterAssn.com Katherine C. Piper Regional Managing Counsel CALPINE COPORATION 4160 DUBLIN BLVD., STE. 100 DUBLIN CA 94568 (925) 557-2252 Katherine.Piper@Calpine.com Avis Kowalewski Vp - Gov'T & Regulatory Affairs CALPINE CORPORATION 4160 DUBLIN BLVD, SUITE 100 DUBLIN CA 94568 (925) 557-2284 Avis.Kowalewski@Calpine.com CAMERON-DANIEL, P.C. EMAIL ONLY EMAIL ONLY CA 00000 Team@Cameron-Daniel.com Gregory Reiss CENTENUS GLOBAL MANAGEMENT, LP 437 MADISON AVENUE, SUITE 19B NEW YORK NY 10022 (212) 763-0909 Gregory.Reiss@CentenusLP.com Stephen R. Cieslewicz Uvm Consultant EMAIL ONLY EMAIL ONLY CA 00000 (707) 591-6862 Steve@UtilityArborist.net |
| Frank Lindh Attorney CITIZENS ENERGY CORPORATION 110 TAYLOR STREET SAN RAFAEL CA 94901 (415) 596-3931 FrankRichLindh@gmail.com For: Citizens Energy Corporation ____________________________________________ William K. Sanders Deputy City Attorney CITY AND COUNTY OF SAN FRANCISCO CITY HALL RM 234 1 DR. CARLTON B. GOODLETT PLACE SAN FRANCISCO CA 94102-4682 (415) 554-6771 William.Sanders@sfCityAtty.org For: City and County of San Francisco ____________________________________________ William R. Smith City Mgr CITY OF COLTON 650 N. LA CADENA DRIVE COLTON CA 92324 (909) 370-5099 For: City of Colton ____________________________________________ John Driscoll City Attorney CITY OF PLACERVILLE 31001 CENTER STREET PLACERVILLE CA 95667 (530) 642-5200 JDriscoll@CityOfPlacerville.org For: City of Placerville ____________________________________________ Yue-Han Chow Sr. Deputy City Attorney CITY OF SAN JOSE 200 E. SANTA CLARA STREET, 16TH FL SAN JOSE CA 95113 (408) 535-1201 Yue-Han.Chow@SanJoseCa.gov Elisa Tolentino Sr. Deputy City Attorney CITY OF SAN JOSE' OFFICE OF THE CITY ATTORNEY 200 EAST SANTA CLARA STREET, 16TH FL. SAN JOSÃ‰ CA 95113 (408) 535-1953 Elisa.Tolentino@SanJoseCa.gov | Adam Abel Assist. City Attorney CITY OF SANTA ROSA 100 SANTA ROSA AVENUE, RM 8 SANTA ROSA CA 95404 (707) 543-3050 SGallagher@SRcity.org Sue A. Gallagher City Attorney CITY OF SANTA ROSA 100 SANTA ROSA AVE., RM 8 SANTA ROSA CA 95404 (707) 543-3050 SGallagher@SRcity.org Mark T. Prestwich City Mgr CITY OF ST. HELENA 1480 MAIN STREET ST. HELENA CA 94574 (707) 312-0252 MPrestwich@CityofStHelena.org For: City of St. Helena ____________________________________________ Kevin Collins PO BOX 722 FELTON CA 95018 (831) 234-7306 Europa@Cruzio.com For: Kevin Collins ____________________________________________ Mary Neher District Secretary CONTRA COSTA WATER DISTRICT PO BOX H20 CONCORD CA 94524 (925) 688-8024 MNeher@CCwater.com Mark P. Schreiber Attorney COOPER, WHITE & COOPER LLP 201 CALIFORNIA STREET, 17TH FL. SAN FRANCISCO CA 94111 (415) 433-1900 MSchreiber@cwcLaw.com |
| John R. Todd Dep. Chief-Prevention Svcs. Bureau COUNTY OF LOS ANGELES FIRE DEPT. 1320 N. EASTERN AVENUE, RM. 254 LOS ANGLELES CA 90063-3294 (323) 881-2461 John.Todd@Fire.LAcounty.gov For: County of Los Angeles ____________________________________________ Katharine L. Elliott County Counsel COUNTY OF MENDOCINO 501 LOW GAP ROAD, RM 1030 UKIAH CA 95482 (707) 234-6885 ElliottK@co.mendocino.ca.us For: County of Mendocino ____________________________________________ Elizabeth G. Pianca Lead Deputy County Counsel COUNTY OF SANTA CLARA 70 W. HEDDING ST., EAST WING, 9TH FL. SAN JOSE CA 95110 (408) 299-5900 Elizabeth.Pianca@CCO.SCCgov.org Steve M. Mitra Assist. County Counsel COUNTY OF SANTA CLARA 70 W. HEDDING ST., EAST WING, 9TH FL. SAN JOSE CA 95110 (408) 299-5900 Steve.Mitra@CCO.SCCgov.org For: County of Santa Clara ____________________________________________ Bruce Goldstein County Counsel COUNTY OF SONOMA 575 ADMINISTRATION DRIVE, ROOM 105-A SANTA ROSA CA 95403 (707) 565-2421 Bruce.Goldstein@sonoma-county.org Cory Oâ€™Donnell Chief Deputy County Counsel COUNTY OF SONOMA 575 ADMINISTRATION DRIVE, ROOM 105-A SANTA ROSA CA 95403 (707) 565-2421 Cory.ODonnell@sonoma-county.org | Petra Bruggisser Deputy County Counsel COUNTY OF SONOMA 575 ADMINISTRATION DRIVE, ROOM 105-A SANTA ROSA CA 94503 (707) 565-2421 Petra.Bruggisser@sonoma-county.org Esther Northrup State Regulatory Affairs COX CALIFORNIA TELCOM, LLC 5887 COPLEY DRIVE, STE. 300 SAN DIEGO CA 92111 (858) 836-7308 Esther.Northrup@cox.com CPUC - LEGAL EMAIL ONLY EMAIL ONLY CA 00000 AppRhg@cpuc.ca.gov Paul Schulman Sr Research Fellow CTR FOR CATASTROPHIC RISK MGNT MILLS COLLEGE UNIVERSITY OF CALIFORNIA BERKELEY CA 94720 (925) 376-7682 Paul@Mills.edu Shelby Chase Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5402 sz2@cpuc.ca.gov Franz Cheng Energy Division AREA 4-A 300 Capitol Mall Sacramento CA 95814 4309 (415) 703-1536 fcc@cpuc.ca.gov Christopher Chow Executive Division RM. 5301 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2234 crs@cpuc.ca.gov |
| Charles Christiansen Communications Division AREA 3-E 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3212 chc@cpuc.ca.gov Carolina Contreras Safety Policy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5125 ccg@cpuc.ca.gov Cheryl Cox Energy Division 300 Capitol Mall Sacramento CA 95814 4309 (916) 327-6799 cxc@cpuc.ca.gov DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, STE. 800 SAN FRANCISCO CA 94111 (415) 276-6587 DWTcpucDockets@dwt.com Anna Fero Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111 (415) 276-6500 AnnaFero@dwt.com David Huang Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111 (415) 276-6500 DavidHuang@dwt.com I Sultan Associate DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, STE. 800 SAN FRANCISCO CA 94111 (415) 276-6539 TahiyaSultan@dwt.com | Jim Tomlinson DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111 (415) 276-6587 JimTomlinson@dwt.com Patrick Ferguson Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111 (415) 276-6500 PatrickFerguson@dwt.com Steve Greenwald Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, STE. 800 SAN FRANCISCO CA 94111 (415) 276-6500 SteveGreenwald@dwt.com For: AD HOC Committee of Sr Unsecured Noteholders of PG&E: Angelo, Gordon & Co., LP; Apollo Global Management LLC; Aurelius Capital Mgnt, LP; Canyon Capital Advisors LLC; Capital Group; Carval Investors; Castle Hook Partners LLP; Citadel Advisors LLC; Citigroup Global Markets: Cyrus Capital Partners, LP; Davidson Kempner Capital Mgnt LP; Deutsche Bank Securities Inc.; Diameter Capital Partners LP; Elliott Mgnt Corp; Farallon Capital Mgnt LLC; Fir Tree Partners; Oaktree Capital Mgnt, LP; Och-Ziff Capital Mgnt Group LLC; Pacific Investment Mgnt Co. LLC; Pacific Life Ins. Co; P. Schoenfeld Asset Mgnt LP; Senator Investment Group LP; Taconic Capital Advisors LP; Third Point LLC; and Varde Partners, Inc. ____________________________________________ Suzanne Toller Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111-6533 (415) 276-6500 SuzanneToller@dwt.com Vidhya Prabhakaran Attorney DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY ST., STE. 800 SAN FRANCISCO CA 94111 (415) 276-6500 VidhyaPrabhakaran@dwt.com For: AD HOC Committee of Sr Unsecured Noteholders of PG&E: Angelo, Gordon & Co., LP; Apollo Global Management LLC; Aurelius Capital Mgnt, LP; Canyon Capital Advisors LLC; Capital Group; Carval Investors; Castle Hook Partners LLP; Citadel Advisors LLC; Citigroup Global Markets: Cyrus Capital Partners, LP; Davidson Kempner Capital Mgnt LP; Deutsche Bank Securities Inc.; Diameter Capital Partners LP; Elliott Mgnt Corp; Farallon Capital Mgnt LLC; Fir Tree Partners; Oaktree Capital Mgnt, LP; Och-Ziff Capital Mgnt Group LLC; Pacific Investment Mgnt Co. LLC; Pacific Life Ins. Co; P. Schoenfeld Asset Mgnt LP; Senator Investment Group LP; Taconic Capital Advisors LP; Third Point LLC; and Varde Partners, Inc. ____________________________________________ Katie Jorrie Attorney DAVIS WRIGHT TREMAINE, LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111 (415) 276-6500 KatieJorrie@dwt.com |
| John W. Leslie, Esq Attorney DENTONS US LLP EMAIL ONLY EMAIL ONLY CA 92121 (619) 699-2536 John.Leslie@dentons.com Daniel W. Douglass Attorney At Law DOUGLASS & LIDDELL 4766 PARK GRANADA, SUITE 209 CALABASAS CA 91302 (818) 961-3001 Douglass@EnergyAttorney.com Michael Kramer DUCERA PARTNERS LLC 499 PARK AVENUE, 16TH FLOOR NEW YORK NY 10022 (212) 671-9750 cpuc@DuceraPartners.com Donald R. Allen Founding Partner, Counsel DUNCAN & ALLEN 1730 RHODE ISLAND AVENUE, NW, SUITE 700 WASHINGTON DC 20036 (202) 289-8400 DRA@DuncanAllen.com For: Citizens Transmission LLC ____________________________________________ Fadi Daye Safety and Enforcement Division 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 576-7017 ffd@cpuc.ca.gov For: SED Marianne Divina Administrative Law Judge Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 696-7307 md9@cpuc.ca.gov Tim G. Drew Public Advocates Office AREA 4-A 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5618 zap@cpuc.ca.gov | Drucilla Dunton Safety and Enforcement Division 300 Capitol Mall Sacramento CA 95814 4309 (916) 327-6775 dd4@cpuc.ca.gov Anand Durvasula Executive Division RM. 5130 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2765 ad1@cpuc.ca.gov Rachel Jones EAST BAY MUNICIPAL UTILITY DISTRICT 375 ELEVENTH STREET OAKLAND CA 94607 (510) 287-0166 Rachel.Jones@EBmud.com Saji Thomas Pierce EAST BAY MUNICIPAL UTILITY DISTRICT 375 11TH STREET OAKLAND CA 94607-4240 (510) 287-2013 Saji.Pierce@EBmud.com Brett T. Kawakami EBMUD 375 11TH STREET, STE. 200 OAKLAND CA 94541 (510) 287-1087 Brett.Kawakami@EBmud.com Brian S. Biering Attorney ELLISON SCHNEIDER HARRIS & DONAN LLP 2600 CAPITOL AVE., STE. 400 SACRAMENTO CA 95816-5931 (916) 447-2166 BSB@esLawFirm.com For: DATC Path 15, LLC ____________________________________________ Andrew B. Brown ELLISON SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVENUE, STE. 400 SACRAMENTO CA 95816 (916) 447-2166 abb@eslawfirm.com |
| Jeffery D. Harris Attorney ELLISON SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVENUE, STE. 400 SACRAMENTO CA 95816 (916) 447-2166 JDH@eslawfirm.com Ronald Liebert Attorney ELLISON, SCHNEIDER HARRIS & DONLAN LLP 2600 CAPITOL AVE., STE. 400 SACRAMENTO CA 95816 (916) 447-2166 RL@esLawFirm.com For: Perimeter Solutions ____________________________________________ Laura J. Manz Director ENERGY NAVIGANT 35 IRON POINT CIRCLE, STE. 225 FOLSOM CA 95630 (858) 354-8333 Laura.Manz@Navigant.com Amanda Vanega EQ RESEARCH LLC 1155 KILDAIRE FARM ROAD, SUITE 203 CARY NC 27511 (919) 825-3339 AVanega@EQ-research.com Blake Elder Policy Research Analyst EQ RESEARCH, LLC 1155 KILDAIRE FARM ROAD, SUITE 202-203 CARY NC 27511 (919) 825-3339 CPUCdockets@EQ-research.com Ray Cruz Dir ERGONICA 1107 FAIR OAKS AVE., STE. 887 SOUTH PASADENA CA 91030 (213) 598-7430 Ray.Cruz@Ergonica.com For: Ergonica ____________________________________________ | Katherine Palmquist EXPONENT EMAIL ONLY EMAIL ONLY CA 00000 kpalmquist@exponent.com Julia Ende Energy Division 300 Capitol Mall Sacramento CA 95814 4309 (415) 703-1688 je6@cpuc.ca.gov Gary C. Ermann Safety Policy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1429 gce@cpuc.ca.gov Jean Hawley Telecommunications Paralegal FRIEND, HUDAK & HARRIS, LLP THREE RAVINIA DRIVE, STE. 1700 ATLANTA GA 30346-2131 (770) 399-9500 JHawley@FH2.com Amy Warshauer Mgr - Gov'T & External Affairs FRONTIER COMMUNICATIONS 1201 K STREET, SUITE 1980 SACRAMENTO CA 95814 (916) 683-7989 Amy.Warshauer@ftr.com Charlie Born FRONTIER COMMUNICATIONS 1201 K STREET, STE. 1980 SACRAMENTO CA 95814 (916) 686-3570 Charlie.Born@FTR.com Arthur Fisher Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2056 aei@cpuc.ca.gov |
| Masoud Foudeh Energy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1244 mf5@cpuc.ca.gov Jonathan Frost Energy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5412 jf6@cpuc.ca.gov Brian T. Cragg Attorney GOODIN, MACBRIDE, SQUERI & DAY, LLP 505 SANSOME STREET, SUITE 900 SAN FRANCISCO CA 94111 (415) 392-7900 BCragg@GoodinMacBride.com Michael B. Day Attorney GOODIN, MACBRIDE, SQUERI, DAY & LAMPREY, 505 SANSOME ST., STE. 900 SAN FRANCISCO CA 94111 (315) 392-7900 MDay@GoodinMacBride.com For: Trans-Elect NTD Path 15, LLC ____________________________________________ Zoe Harrold GREEN POWER INSTITUTE 2039 SHATTUCK AVE., STE. 402 BERKELEY CA 94704 ZHarrold@gmail.com Marc Kolb GRID DEL SOL CONSULTING 46 VISTA DEL SOL MILL VALLEY CA 94941 (707) 385-1624 delsolgrid@gmail.com Asish Gautam Safety Policy Division RM. 4-44 300 Capitol Mall Sacramento CA 95814 4309 (916) 823-4834 agt@cpuc.ca.gov | Elena Gekker Legal Division RM. 5137 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1642 egk@cpuc.ca.gov Pouneh Ghaffarian Legal Division RM. 5025 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1317 pxg@cpuc.ca.gov Daphne Goldberg Public Advocates Office RM. 4208 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1578 dk4@cpuc.ca.gov Alice L. Harron Ceo HARRON, LLC 4016 EVERETT AVE. OAKLAND CA 94602 (415) 420-5707 AHarron@HarronLLC.com Emily Lieban HOLLAND & KNIGHT LLP 50 CALIFORNIA STREET, STE. 2800 SAN FRANCISCO CA 94111 (415) 743-6946 emily.lieban@hklaw.com Kevin J. Ashe Associate HOLLAND & KNIGHT LLP 50 CALIFORNIA STREET, STE. 2800 SAN FRANCISCO CA 94111 (415) 743-6921 Kevin.Ashe@HKlaw.com Tara Kaushik Partner HOLLAND & KNIGHT LLP 50 CALIFORNIA STREET, SUITE 2800 SAN FRANCISCO CA 94111 (415) 743-6924 Tara.Kaushik@HKlaw.com |
| Marcos Mora Director Of Development HORIZON WEST TRANSMISSION EMAIL ONLY EMAIL ONLY AA 00000 (561) 691-2162 marcos.mora@nee.com Scott Castro HORIZON WEST TRANSMISSION, LLC ONE POST STREET, SUITE 2550 SAN FRANCISCO CA 94104 (415) 318-5919 scott.castro@nee.com For: (Formerly NextEra Energy Transmission, LLC) ____________________________________________ Steven Greco Regulatory Affairs Analyst HORIZON WEST TRANSMISSION, LLC 700 UNIVERSE BLVD JUNO BEACH FL 33407 (561) 691-7481 Steven.Greco@NextEraEnergy.com For: (Formerly NextEra Energy Transmission, LLC) ____________________________________________ Tracy C. Davis Sr. Attorney HORIZON WEST TRANSMISSION, LLC 5920 W. WILLIAM CANNON DR., BLDG. 2 AUSTIN TX 78749 (512) 236-3141 Tracy.C.Davis@NextEraEnergy.com For: (formerly NextEra Energy Transmission, LLC) ____________________________________________ Robert Haga Administrative Law Judge Division RM. 5006 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2538 rwh@cpuc.ca.gov Jessica T. Hecht Administrative Law Judge Division 400 R Street Sacramento CA 95814 6200 (415) 703-2027 jhe@cpuc.ca.gov | Christopher Hogan Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2848 ch6@cpuc.ca.gov Tyler Holzschuh Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2717 tyh@cpuc.ca.gov Landis Marttila IBEW 1245 30 ORANGE TREE CIRCLE VACAVILLE CA 95687 (925) 285-9057 LKM4@ibew1245.com Curt Barry Sr Writer / Editor INSIDE WASHINGTON PUBLISHERS EMAIL ONLY EMAIL ONLY CA 00000 (916) 449-6171 CBarry@iwpnews.com Craig Judson Mcbeth JUDSON INVESTMENTS LLC 84 WEST PARK PLACE, 3RD FL. STAMFORD CT 06901 (203) 343-0367 CJM@JudsonLLC.com Caroline Thomas Jacobs Wildfire Safety Division RM. 520 300 Capitol Mall Sacramento CA 95814 4309 (916) 894-5607 ctj@cpuc.ca.gov Buck B. Endemann Partner K&L GATES LLP 4 EMBARCADERO CENTER, STE. 1200 SAN FRANCISCO CA 94111 (415) 882-8016 Buck.Endemann@KLGates.com |
| Scott Dunbar Attorney KEYES & FOX LLP 1580 LINCOLN STREET, STE. 880 DENVER CO 80203 (949) 525-6016 SDunbar@KeyesFox.com Sheridan Pauker Partner KEYES & FOX LLP 436 14TH STREET, SUITE 1305 OAKLAND CA 94612 (510) 314-8202 SPauker@KeyesFox.com Valerie Kao Administrative Law Judge Division RM. 5005 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1341 vuk@cpuc.ca.gov Jonathan Koltz Executive Division RM. 5035 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2760 jk5@cpuc.ca.gov Brian Korpics Executive Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5219 bk4@cpuc.ca.gov Jeffery A. Williams Superintendent - Codes & Ordinances L.A. DEPT OF WATER & POWER 111 NORTH HOPE STREET, RM. 856 LOS ANGELES CA 90012 (213) 367-2212 Jeffery.Williams@ladwp.com Shannon Eddy Exe Dir LARGE-SCALE SOLAR ASSOCIATION 2501 PORTOLA WAY SACRAMENTO CA 95818 (415) 819-4285 eddyconsulting@gmail.com | Tim Mason Policy Dir LARGE-SCALE SOLAR ASSOCIATION 2501 PORTOLA WAY SACRAMENTO CA 95818 (510) 812-1416 Tim@LargeScaleSolar.org Michael Brown Consultant LAW OFFICE OF MICHAEL BROWN EMAIL ONLY EMAIL ONLY CA 00000 (415) 699-0261 Michael@MBrownLaw.net For: Small Business Utility Advocates (SBUA) ____________________________________________ Leon Bloomfield Attorney LAW OFFICES OF LEON BLOOMFIELD 1901 HARRISON STREET, SUITE 1400 OAKLAND CA 94612 (510) 625-8250 lmb@wblaw.net C. Susie Berlin Attorney LAW OFFICES OF SUSIE BERLIN 1346 THE ALAMEDA, SUITE 7-141 SAN JOSE CA 95126 (408) 778-8478 Berlin@SusieBerlinLaw.com Gerron Blackwell LIBERTY UTILITIES 9750 WASHBURN ROAD DOWNEY CA 90241 Gerron.Blackwell@LibertyUtilities.com Greg Campbell LIBERTY UTILITIES 9750 WASHBURN ROAD DOWNEY CA 90241 Greg.Campbell@LibertyUtilities.com Annmarie Lett Coordinator - Rates & Reg Affairs LIBERTY UTILITIES (CALIFORNIA) 9750 WASHBURN ROAD DOWNEY CA 90241 (562) 319-4751 AnnMarie.Lett@LibertyUtilities.com |
| Sharon Yang Dir - Legal Services LIBERTY UTILITIES (CALPECO ELECTRIC) LLC 9750 WASHBURN ROAD DOWNEY CA 90241 (562) 299-5120 Sharon.Yang@LibertyUtilities.com For: Liberty Utilities (California) ____________________________________________ Jamie Garcia LOS ANGELES DEPT OF WATER AND POWER 11 N. HOPE ST. ROOM 856 LOS ANGELES CA 90012 (213) 367-2212 jaimer.garcia@ladwp.com Jim Rainey Staff Writer LOS ANGELES TIMES EMAIL ONLY EMAIL ONLY CA 00000 (213) 237-3395 jim.rainey@LAtimes.com Jessie Crozier LUMINUS MANAGEMENT 350 WEST 43RD APT 14F NEW YORK NY 10036 (248) 252-0793 utilitydockets@gmail.com Diana L. Lee Legal Division RM. 4107 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-4342 dil@cpuc.ca.gov Aaron Louie Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 696-7316 aar@cpuc.ca.gov Chloe Lukins Public Advocates Office RM. 4102 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1637 clu@cpuc.ca.gov | Joseph W. Mitchell, Ph.D M-BAR TECHNOLOGIES AND CONSULTING, LLC 19412 KIMBALL VALLEY RD. RAMONA CA 92065 (760) 703-7521 JWMitchell@MBarTek.com Steven Moss Partner M.CUBED 296 LIBERTY STREET SAN FRANCISCO CA 94114 (415) 643-9578 steven@moss.net For: The Local Government Sustainable Energy Coalition ____________________________________________ Alejandro Mendez MADISON AVENUE PARTNERS 150 EAST 58TH STREET, 14TH FLOOR NEW YORK NY 10155 (212) 702-8646 AM@MadisonAvelp.com Eli Samaha MADISON AVENUE PARTNERS 150 E 58TH STREET, 14TH FLOOR NEW YORK NY 10155 (212) 702-8648 Eli@MadisonAvelp.com Michael Callahan MARIN CLEAN ENERGY EMAIL ONLY EMAIL ONLY CA 00000 mcallahan@mcecleanenergy.org Stephen Keehn Mgr Of Energy Reg & Legislative Affairs MONTEREY BAY COMMUNITY POWER 70 GARDEN COURT, SUITE 300 MONTEREY CA 93940 (831) 641-7222 skeehn@mbcp.org MRW & ASSOCIATES, LLC EMAIL ONLY EMAIL ONLY CA 00000 (510) 834-1999 MRW@MRWassoc.com |
| Christopher Moore Executive Division 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 576-7095 cm8@cpuc.ca.gov Candace Morey Legal Division RM. 5031 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3211 cjm@cpuc.ca.gov Lucy Morgans Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 696-7333 lym@cpuc.ca.gov April Mulqueen Executive Division RM. 5220 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1112 am4@cpuc.ca.gov Trina Horner Director NAVIGANT CONSULTING 101 CALIFORNIA STREET, STE. 4100 SAN FRANCISCO CA 94111 (415) 399-2107 Trina.Horner@Navigant.com Edwin Guyandi Analyst NEWTYN MANAGEMENT 405 PARK AVENUE, SUITE 1104 NEW YORK NY 10022 (212) 446-2477 Edwin@Newtyn.com James W. Carson Attorney At Law NIELSEN MERKSAMER PARRINELLO 2350 KERNER BLVD., STE250 SAN RAFAEL CA 94901 (415) 389-6800 jcarson@nmgovlaw.com | Karin Nguyen Safety and Enforcement Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2924 kny@cpuc.ca.gov Jay Barkman ORANGE COUNTY FIRE AUTHORITY 1 FIRE AUTHORITY ROAD IRVINE CA 92602 (714) 573-6048 jaybarkman@ocfa.org Jamie Ormond Executive Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1193 jo2@cpuc.ca.gov Case Coordination PACIFIC GAS AND ELECTRIC COMPANY PO BOX 770000; MC B23A SAN FRANCISCO CA 94177 (415) 973-6593 RegRelcpucCases@pge.com Charles R. Middlekauff PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B30A / BOX 7442 SAN FRANCISCO CA 94105 (415) 973-6971 Charles.Middlekauff@pge.com Gareth Stamp PACIFIC GAS AND ELECTRIC COMPANY 245 MARKET STREET, ROOM 914C SAN FRANCISCO CA 94105 GRSL@pge.com Jessica Basilio, Esq. Attorney PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B30A SAN FRANCISCO CA 94105 (415) 973-5548 Jessica.Basilio@pge.com Julie Cerio PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE ST., RM. 2388B SAN FRANCISCO CA 94104 (415) 973-2079 JQCH@pge.com |
| Lise H. Jordan Attorney At Law PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B30A SAN FRANCISCO CA 94105 (415) 973-6965 LHJ2@pge.com Meghan Dewey Mgr - Ee Policy / Strategy PACIFIC GAS AND ELECTRIC COMPANY EMAIL ONLY EMAIL ONLY CA 00000 (415) 973-1805 Meghan.Dewey@pge.com Meredith Allen Sr. Director, Regulatory Relations PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B10C SAN FRANCISCO CA 94105 (415) 973-2868 MEAe@pge.com Spencer Olinek PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, ROOM 2333 SAN FRANCISCO CA 94105 (415) 973-5540 WSO3@pge.com Tracy Maratukulam PACIFIC GAS AND ELECTRIC COMPANY 245 MARKET STREET, ROOM 903 SAN FRANCISCO CA 94105 (415) 973-3638 TDM9@pge.com Viktoriya Malkina Coordinator - Regulatory PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, MC B23A SAN FRANCISCO CA 94105 (415) 973-1818 V2M4@pge.com Wade A. Greenacre Case Mgr. PACIFIC GAS AND ELECTRIC COMPANY EMAIL ONLY EMAIL ONLY CA 00000 (415) 973-8098 wag9@pge.com | William V. Manheim Attorney At Law PACIFIC GAS AND ELECTRIC COMPANY PO BOX 770000, MAIL CODE B30A SAN FRANCISCO CA 94177 (415) 973-6628 WVM3@pge.com Heide Marie Caswell PACIFICORP 825 NE MULTNOMAH, STE. 1700 PORTLAND OR 97232 (503) 813-6216 Heide.Caswell@PacifiCorp.com Jessica Buno Ralston Sr. Attorney PACIFICORP 825 NE MULTNOMAH, SUITE 2000 PORTLAND OR 97232 (503) 813-5817 Jessica.Ralston@PacifiCorp.com Pooja Kishore Mgr - Regulatory Affairs PACIFICORP 825 NE MULTNOMAH STREET, SUITE 2000 PORTLAND OR 97232 (503) 813-7314 CaliforniaDockets@PacifiCorp.com Timothy K. Clark PACIFICORP (ROCKY MOUNTAIN POWER) 1407 WEST NORTH TEMPLE, SUITE 320 SALT LAKE CITY UT 84116 (801) 220-4565 Tim.Clark@pacificorp.com Doug Karpa Sr Analyst - Regulatory PENINSULA CLEAN ENERGY 2075 WOODSIDE ROAD REDWOOD CITY CA 94061 (650) 771-9093 DKarpa@PeninsulaCleanEnergy.com Joseph F. Wiedman Dir - Regulatory & Legislative Affairs PENINSULA CLEAN ENERGY AUTHORITY 2075 WOODSIDE ROAD REDWOOD CITY CA 94061 (650) 265-0083 JWiedman@PeninsulaCleanEnergy.com |
| Nori Yokozuka General Counsel PERIMETER SOLUTIONS 8000 MARYLAND AVE., SUITE 350 CLAYTON MO 63105 (314) 396-7314 Noriko.Yokozuka@perimeter-solutions.com James W. Mctarnaghan Attorney PERKINS COIE LLP 505 HOWARD STREET, STE. 1000 SAN FRANCISCO CA 94105 (415) 344-7007 ServiceList.cpuc@PerkinsCoie.com Monica Palmeira Executive Division RM. 3-90 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1268 mp8@cpuc.ca.gov Leslie L. Palmer Safety and Enforcement Division RM. 2203 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2369 llp@cpuc.ca.gov For: SED Christopher Parkes Public Advocates Office AREA 2-D 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1975 cjp@cpuc.ca.gov Bryan Pena Safety and Enforcement Division 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 620-2680 bp1@cpuc.ca.gov Joceline Pereira Safety and Enforcement Division 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 266-4720 jcn@cpuc.ca.gov | Quang Pham Safety and Enforcement Division AREA 2-D 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-4763 qap@cpuc.ca.gov Filiberto A. Pineda Executive Division 300 Capitol Mall Sacramento CA 95814 4309 (916) 823-4778 fil@cpuc.ca.gov Elizabeth Podolinsky Safety and Enforcement Division RM. 5216 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3201 pod@cpuc.ca.gov Nathan Poon Administrative Law Judge Division RM. 5013 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2751 np2@cpuc.ca.gov Jim Ross RCS, INC. 266 PENNINGTON LANE CHESTERFIELD MO 63005 (314) 530-9544 JimRoss@r-c-s-inc.com Allie Detrio REIMAGINE POWER 77 SALA TERRACE SAN FRANCISCO CA 94112 (415) 825-0133 Allie@Reimagine-Power.com Conor Skelding Reporter REORG 11 E 26TH STREET, 12TH FL. NEW YORK NY 10010 (646) 390-5733 CSkelding@Reorg.com |
| Nick Williams Senior Distressed Debt Analyst REORG RESEARCH INC. EMAIL ONLY EMAIL ONLY NY 00000 (646) 862-2577 NWilliams@reorg.com Sue Mara Consultant RTO ADVISORS, L.L.C. 164 SPRINGDALE WAY REDWOOD CITY CA 94062 (415) 902-4108 Sue.Mara@RTOadvisors.com Junaid Rahman Safety Policy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3372 jnr@cpuc.ca.gov James Ralph Executive Division RM. 5037 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-4673 jr8@cpuc.ca.gov Jonathan J. Reiger Legal Division RM. 4107 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 355-5596 jzr@cpuc.ca.gov Colin Rizzo Administrative Law Judge Division RM. 5042 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1784 cr2@cpuc.ca.gov Joy Mastache Sr. Attorney - Off. Of Gen. Counsel SACRAMENTO MUNICIPAL UTILITY DISTRICT 6201 S STREET, MS B406 SACRAMENTO CA 95817 (916) 732-5906 Joy.Mastache@smud.org | Central Files SAN DIEGO GAS & ELECTRIC COMPANY 8330 CENTURY PARK CT, CP31-E SAN DIEGO CA 92123-1530 (858) 654-1240 CentralFiles@SempraUtilities.com Christopher M. Lyons Sr. Counsel SAN DIEGO GAS & ELECTRIC COMPANY 8326 CENTURY PARK COURT, CP32D SAN DIEGO CA 92123 (858) 654-1559 CLyons@sdge.com Chuck Manzuk Dir - Grc & Revenue Requirements SAN DIEGO GAS & ELECTRIC COMPANY 8330 CENTURY PARK COURT SAN DIEGO CA 92123 (858) 654-1782 CManzuk@SempraUtilities.com Jamie K. York Grc Program Mgr. SAN DIEGO GAS & ELECTRIC COMPANY 8330 CENTURY PARK COURT, CP32D SAN DIEGO CA 92123 (858) 654-1739 JYork@SempraUtilities.com Norma Jasso Mgr - Regulatory SAN DIEGO GAS & ELECTRIC COMPANY 8330 CENTURY PARK CT, CP31E SAN DIEGO CA 92123 (858) 654-3535 NJasso@SempraUtilities.com SAN DIEGO GAS AND ELECTRIC COMPANY 8330 CENTURY PARK COURT (CP31E) SAN DIEGO CA 92123-1548 (858) 654-1240 CentralFiles@SempraUtilities.com Ross Nakasone Planning & Regulatory Compliance SAN FRANCISCO PUBLIC UTILITES COMMISSION 525 GOLDEN GATE AVE., 7TH FL. SAN FRANCISCO CA 94102 (415) 554-2436 RNakasone@SFwater.org |
| Ilana Parmer Mandelbaum Deputy County Counsel SAN MATEO COUNTY COUNSEL'S OFFICE 400 COUNTY CENTER, 6TH FLOOR REDWOOD CITY CA 94063 (650) 363-4681 imandelbaum@smcgov.org Phillip Muller President SCD ENERGY SOLUTIONS 436 NOVA ALBION WAY SAN RAFAEL CA 94903 (415) 479-1710 PhilM@SCDenergy.com William Chung Vice President Business Development SHARPER SHAPE 1080 NIMITZ AVE SUITE 200 VALLEJO CA 94592 (714) 423-1799 will.chung@sharpershape.com Kerri Timmer SIERRA BUISNESS COUNCIL 10183 TRUCKEE AIRPORT RD TRUCKEE CA 96161 (530) 414-8247 KTimmer@sierrabusiness.org Ariel Strauss SMALL BUSINESS UTILITY ADVOCATES 548 MARKET ST., SUITE 11200 SAN FRANCISCO CA 94104 (310) 709-1213 ariel@utilityadvocates.org Audra Hartmann Principal SMITH, WATTS & HARTMANN 925 L STREET, SUITE 220 SACRAMENTO CA 95814 (916) 446-5508 AHartmann@SWMconsult.com Case Administration SOUTHERN CALIFORNIA EDISON COMPANY 8631 RUSH STREET ROSEMEAD CA 91770 (626) 302-6906 Case.Admin@sce.com | Connor Flannigan SOUTHERN CALIFORNIA EDISON COMPANY 2244 WALNUT GROVE AVE. ROSEMEAD CA 91770 connor.flanigan@sce.com Gary Stern Managing Dir. SOUTHERN CALIFORNIA EDISON COMPANY 8631 RUSH STREET ROSEMEAD CA 91770 (626) 302-6904 Gary.Stern@sce.com For: Southern California Edison Company ____________________________________________ Laura Genao Dir. - Cpuc Regulatory Affairs SOUTHERN CALIFORNIA EDISON COMPANY 601 VAN NESS AVE., STE. 2030 SAN FRANCISCO CA 94102 (626) 302-3062 Laura.Genao@sce.com Margarita Gevondyan Sr. Attorney SOUTHERN CALIFORNIA EDISON COMPANY 2244 WALNUT GROVE AVE / PO BOX 800 ROSEMEAD CA 91770 (626) 302-6931 Margarita.Gevondyan@sce.com For: Southern California Edison Company ____________________________________________ Ryan Stevenson Principal Advisor / Reg - Policy SOUTHERN CALIFORNIA EDISON COMPANY 8631 RUSH ST., GEN. OFFICE 4 ROSEMEAD CA 91770 Ryan.Stevenson@sce.com Corky Whipple SOUTHWIRE COMPANY, LLC 1 SOUTHWIRE DRIVE CARROLLTON GA 30119 (770) 832-5550 corky.whipple@southwire.com Laura Mcwilliams STATE SENATOR JERRY HILL STATE CAPITOL, ROOM 5035 SACRAMENTO CA 95814 (916) 651-4013 Laura.McWilliams@sen.ca.gov |
| Melissa K. Semcer Wildfire Safety Division RM. 522 400 R Street Sacramento CA 95814 6200 (916) 823-4773 unc@cpuc.ca.gov Sean A. Simon Executive Division RM. 5201 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3791 svn@cpuc.ca.gov Nathaniel Skinner Public Advocates Office AREA 4-A 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1393 nws@cpuc.ca.gov Joyce Steingass Energy Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1810 jws@cpuc.ca.gov Katherine J. Stockton Executive Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1711 kjs@cpuc.ca.gov Eric Borden Energy Policy Analyst THE UTILITY REFORM NETWORK 785 MARKET STREET, STE. 1400 SAN FRANCISCO CA 94103 (415) 929-8876 X320 EBorden@turn.org Katy Morsony Staff Attorney THE UTILITY REFORM NETWORK 785 MARKET STREET, SUITE 1400 SAN FRANCISCO CA 94103 (415) 929-8876 X313 KMorsony@turn.org | Marcel Hawiger Staff Attorney THE UTILITY REFORM NETWORK 785 MARKET ST., STE. 1400 SAN FRANCISCO CA 94103 (415) 929-8876 X311 Marcel@turn.org Robert Finkelstein General Counsel THE UTILITY REFORM NETWORK 785 MARKET ST., STE. 1400 SAN FRANCISCO CA 94103 (415) 929-8876 X-307 BFinkelstein@turn.org Jane E. Terjung Community Advocates TOPANGA COMMUNITY ALLIANCE 1639 OAK DRIVE TOPANGA CA 90290 (310) 488-8779 JaneTerjung@gmail.com Charlotte TerKeurst Safety and Enforcement Division RM. 2201 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-3124 cft@cpuc.ca.gov For: SED Leuwam Tesfai Executive Division RM. 5137 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2403 lt3@cpuc.ca.gov Sarah R. Thomas Administrative Law Judge Division RM. 5033 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2310 srt@cpuc.ca.gov Koko M. Tomassian Wildfire Safety Division 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 576-7099 kmt@cpuc.ca.gov For: SED |
| Rick Tse Safety and Enforcement Division AREA 2-D 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 355-5581 rkt@cpuc.ca.gov Kavya Balaraman Reporter UTILITY DIVE EMAIL ONLY EMAIL ONLY DC 00000 Kavya@UtilityDive.com Ricardo Vega EMAIL ONLY EMAIL ONLY CA 00000 ricardo.vega@nexteraenergy.com Jane Whang Staff Counsel VERIZON 201 SPEAR STREET, 7TH FL. SAN FRANCISCO CA 94105 (415) 778-1022 Jane.Whang@Verizon.com Jesus G. Roman Assist. Gen. Counsel VERIZON 15505 SAND CANYON AVE. D201 IRVINE CA 92618 (949) 286-7202 jesus.g.roman@verizon.com Rebecca M. Vorpe Legal Division RM. 3206 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-4443 rv2@cpuc.ca.gov Lon W. House, Ph.D WATER & ENERGY CONSULTING 10645 N. ORACLE RD., STE 121-216 ORO VALLEY AZ 85737 (530) 676-8956 lwhouse@innercite.com | John W. Hamilton Associate Attorney WINSTON & STRAWN LLP 101 CALIFORNIA ST., 35TH FL. SAN FRANCISCO CA 94111 (415) 591-1000 JWHamilton@Winston.com Joan Weber Safety Policy Division RM. 5TH 320 West 4th Street Suite 500 Los Angeles CA 90013 (213) 266-4729 jw8@cpuc.ca.gov For: OSA Fred G. Yanney, Esq. Attorney YANNEY LAW OFFICE 17409 MARQUARDT AVE. STE. C-4 CERRITOS CA 90703 (562) 926-5050 FredYanney@gmail.com Anna Yang Public Advocates Office 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-2144 ayn@cpuc.ca.gov Amy C. Yip-Kikugawa Legal Division RM. 4107 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-5256 ayk@cpuc.ca.gov Matthew Yunge Safety and Enforcement Division 505 Van Ness Avenue San Francisco CA 94102 3298 (415) 703-1667 myu@cpuc.ca.gov |

Attachment 1:

RES WSD-007 Liberty Appendices .pdf

With CPUC ratification of the WSD’s actions.

The WSD (ultimately the Office of Energy Infrastructure Safety) and the CPUC have complementary regulatory roles to fill in ensuring a strong oversight in reducing the risk of ignition of wildfires from utility infrastructure.   The WSD, CPUC, and other relevant agencies will work together to ensure roles are defined and regulatory outcomes are met.

Decisions 19-05-036, 037, 038, 039, 040 and 041 (May 30, 2019).

Pub. Util. Code § 8386.3 (Wildfire Safety Division), § 326.1 (Wildfire Safety Advisory Board).

A ruling issued on December 19, 2019 in proceeding R.18-10-007 described and attached all of the material electrical corporations were required to use in submitting their 2020 WMPs.

Presentations, agendas and other details of the workshops appear on the Commission’s WMP homepage, located at www. cpuc.ca.gov/wildfiremitigationplans/.

Table 10, in 2020 WMP Attachment 5.xlsx March 6, 2020, https://kwftp.cpuc.ca.gov/#/file/287338.

A recloser is a switching device that is designed to detect and interrupt momentary fault conditions.  The device can reclose automatically and reopen if a fault condition is still detected.

A detailed description of the purpose and use of the maturity model is provided the Guidance Resolution being issued concurrently with the instant Resolution.

Executive Order N-33-20. Available at 
https://covid19.ca.gov/img/Executive-Order-N-33-20.pdf .

https://www.cpuc.ca.gov/covid/. Letters to each electrical corporation are found under the heading:”Other CPUC Actions”, March 27, 2020: Joint Letters to IOUs re: Essential Wildfire and PSPS Mitigation Work.