COM/CRC/sid                 		Mailed 2/16/2007

Decision 07-02-030  February 15, 2007

BEFORE THE PUBLIC UTILITIES COMMISSION OF THE STATE OF CALIFORNIA

| Order Instituting Rulemaking to Revise Commission General Order Number 95 pursuant to D.05-01-030. | Rulemaking 05-02-023 (Filed February 24, 2005) |
| --- | --- |

(See Appendix A for a list of appearances.)

OPINION ADOPTING PROPOSED RULE 94 IN
GENERAL ORDER 95 DEALING WITH INSTALLATION
OF WIRELESS ANTENNAS ON UTILITY POLES

TABLE OF CONTENTS

Title                                                                                                           Page

OPINION ADOPTING PROPOSED RULE 94 IN GENERAL ORDER 95 DEALING WITH INSTALLATION OF WIRELESS ANTENNAS ON UTILITY POLES 	2

1.	Summary	2

2.	Procedural Background	3

3.	Commission Jurisdiction	5

4.  Rule 94 Initial Proposals	6

4.1  Proposal 1 for Rule 94	7

4.2  Proposal 2 for Rule 94	8

4.3  Proposal 3 for Rule 94	8

5.  Disputed Provisions	9

6.  Pole-Top Antennas	9

7.  Settlement Agreement	10

7.1  New Rule 94	11

7.1.1  Marking of an Antenna Operator’s Contact Information	11

7.1.2  Vertical Clearance Levels	12

7.1.3  Antenna Exceptions	13

7.2  Marking and De-energizing Measures	14

7.3  Commission Review of the Settlement	16

8.  Additional Marking and De-energizing Safeguards	16

9.  Implementation of Rule Changes	23

10.  Comments on Alternate Proposed Decision	24

11.  Assignment of Proceeding	26

Findings of Fact	26

Conclusions of Law	29

ORDER	30

APPENDIX 1 – Definition of New GO 95, Rule 20 and Settlement Agreement

APPENDIX A – List of Appearances

OPINION ADOPTING PROPOSED RULE 94 IN
GENERAL ORDER 95 DEALING WITH INSTALLATION
OF WIRELESS ANTENNAS ON UTILITY POLES

# Summary

This decision revises General Order (GO) 95 to establish uniform construction standards for attaching wireless antennas to jointly used poles.  In adopting these revisions, this decision approves an unopposed settlement agreement between the Commission’s Consumer Protection and Safety Division (CPSD); the International Brotherhood of Electrical Workers Local 1245 (IBEW); the Communications Workers of America-Ninth District (Communications Workers); Pacific Gas and Electric Company (PG&E); AT&T California; California Cable & Telecommunications Association (CCTA); ClearLinx Network Corporation (ClearLinx); Crown Castle USA, Inc.; New Cingular Wireless PCS, LLC; NextG Networks of California Inc.; Omnipoint Communications, Inc., dba T-Mobile; Southern California Edison Company (SCE); Sprint Nextel; Verizon California Inc.; Verizon Wireless; and William Adams.

We adopt the Rule 94 agreed to by the settling parties and attached to this decision as Appendix 1.  Rule 94 clearly defines antennas; treats antennas as Class C equipment, thereby establishing many construction requirements; provides additional vertical clearances from other conductors and equipment; maintains vertical clearances from the ground; requires a sign for each antenna installation marked with the contact information of the antenna operator; and calls for each antenna installation to be subject to an agreement with the pole owner(s) that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement.

The settlement agreement approved by this decision adopts additional marking and de-energizing requirements.  First, the settlement requires signatory antenna owners to provide further pole-mounted signage on joint use, utility poles.  This signage describes compliance with the Federal Communications Commission (FCC) exposure limits for each antenna installation and identifies the FCC’s recommended minimum approach distance.  Second, the settlement requires protocols for de-energizing antennas that emit radio frequency (RF) energy in excess of the FCC’s General Population/Uncontrolled maximum exposure limits.

# Procedural Background

On October 2, 2001, the Commission issued R.01-10-001 to revise GO 95 and GO 128, which govern, respectively, the construction of overhead and underground electric supply and communications systems.  Commission staff, industry representatives, labor organizations, and the public conducted 16 months of twice-monthly two- to three-day public workshops throughout California.  A total of 63 proposed changes to existing rules were considered.  Of these, 40 were supported by consensus of the workshop participants, 15 were withdrawn, and eight were in dispute.

On January 13, 2005, the Commission issued Decision (D.) 05-01-030.  The Commission adopted the 40 proposed rule changes supported by consensus, noted the 15 withdrawn proposed rule changes, and discussed and resolved seven of the eight disputed proposed rule changes.  The Commission, however, did not approve a new rule to GO 95 to establish uniform construction standards for attaching wireless antennas to jointly used poles.  Instead, in D.05-01-030, the Commission directed staff to further investigate the issues raised by the wireless antenna rules in this new rulemaking proceeding.

On February 24, 2005, the Commission issued an Order Instituting Rulemaking (OIR) that proposed revisions to GO 95 that would establish uniform construction standards for attaching wireless antennas to jointly used poles and towers.  A prehearing conference (PHC) in this proceeding was conducted on May 24, 2005.  In the PHC, the parties agreed to hire a facilitator, as they had done in the earlier proceeding, and to conduct workshops aimed at achieving consensus on wireless antenna rules.

On June 7, 2005, a Scoping Memo and Ruling of the Assigned Commissioner determined that this proceeding is quasi-legislative.  The evidentiary hearing schedule was established too.

Seven days of workshops were held in San Francisco and Los Angeles.  Approximately 40 to 70 participants, in total representing 20 parties, attended each workshop.  While there was substantial agreement on most rules governing wireless antennas, the parties were unable to reach consensus on all issues.  Accordingly, on September 12, 2005, the parties submitted a joint workshop report that included three alternative proposals for a new Rule 94, along with position statements of the parties.

Following a second PHC on November 14, 2005, the Commission conducted evidentiary hearings on February 7-9, 2006.  At hearing, the Commission heard from nine witnesses and received 22 exhibits into evidence.  Briefs were filed on March 13, 2006, and reply briefs were filed on March 28, 2006, at which time the rulemaking was deemed submitted for Commission decision.  A Proposed Decision was issued on April 25, 2006.

Before the Commission acted on the Proposed Decision, several parties on July 18, 2006, filed a joint petition to set aside submission pursuant to Rule 84 of the Rules of Practice and Procedure to allow the parties to pursue settlement discussions.  The petition was granted on July 20, 2006.

On July 28, 2006, PG&E provided notice of a conference regarding a proposed settlement of the disputed issues in this proceeding.  The conference was held on August 4, 2006.

On August 23, 2006, a settlement agreement was proposed by sixteen of the parties, including CPSD and the two union parties.  An evidentiary hearing to consider the proposal was conducted on September 12, 2006, at the conclusion of which this matter was resubmitted for Commission consideration.

# Commission Jurisdiction

The Public Utilities Code establishes that safety issues may be subject to Commission regulation.  According to Public Utilities Code Section 451, “[e]very public utility shall furnish and maintain such adequate, efficient, just, and reasonable service, instrumentalities, equipment, and facilities … as are necessary to promote the safety, health, comfort, and convenience of its patrons, employees, and the public.”  The Commission is obligated to see that such statutory provisions affecting public utilities are enforced and obeyed.  (Pub. Util. Code § 2101.)  Public Utilities Code Section 761 instructs this Commission to promulgate rules for utilities when safety so requires.

Some parties to this proceeding contend that federal law and regulations may constrain our authority to address certain safety issues.  According to wireless carriers, the Commission was precluded from adopting many of the rules in the prior Proposed Decision, because “regulation of telecommunications facilities based on the potential health effects of RF emissions is subject to federal, rather than state[,] jurisdiction.”  We, however, do not need to address these jurisdictional issues in this decision.  The parts of proposed Rule 94 that raised the most significant preemption issues (RF-related signage and methods of de-energizing antennas) now are addressed by the settlement agreement.  The settlement agreement, therefore, moots these jurisdictional issues.

# 4.  Rule 94 Initial Proposals

All parties agree that today GO 95 does not contain specific rules for the installation of wireless antennas on jointly used utility poles, but uniform rules governing the installation of these wireless antennas should be added to GO 95.  As a result of the workshops, the parties presented us with three preliminary proposals for uniform rules, which we briefly discuss below.

## 4.1  Proposal 1 for Rule 94

Proposal 1 was sponsored by CPSD, IBEW, Communications Workers, PG&E, and San Diego Gas & Electric (SDG&E).  It added a definition of “antenna” to Rule 20 of GO 95 (“a device for emitting and/or receiving radio frequency signals”) and proposed a new Rule 94.  The proposed Rule 94 would require that antennas meet standards applicable to Class C communications equipment; maintain a vertical clearance of 6 feet from supply (electrical) conductors operating at 0-50 kilovolts and clearances of 2 feet (vertical) from communications conductors and (horizontal) from the centerline of the pole; provide a sign identifying the antenna and providing information regarding compliance with the FCC’s maximum permissible exposure limits, and provide a means of controlling or shutting down wireless antennas.  Antennas used by utilities for monitoring their supply system and antennas attached to communication cables would be exempt from Rule 94, although they would need to comply with other GO 95 requirements.

## 4.2  Proposal 2 for Rule 94

Proposal 2 was sponsored by SCE.  It was supported by Crown Castle USA, Inc.; Cingular Wireless; NextG Networks; Sprint Nextel; Omnipoint Communications, Inc., dba T-Mobile; and Verizon Wireless (collectively, the Wireless Group).  Its proposed definition of “antenna” and its proposed requirement that antennas meet the circuit requirements of Class C equipment mirrored the requirements of Proposal 1.  Proposal 2 provided for a vertical separation of 2 feet from communication conductors, a 2-foot horizontal clearance from the face of the pole when supported by a cross arm, and a clearance from supply conductors of 4 to 6 feet as specified in GO 95 tables.  At the evidentiary hearing on February 7, 2006, all parties stipulated that Proposal 2 could be amended to include provision 94.5 of Proposal 1 (a sign identifying the type of antenna and a 24-hour contact number for the antenna operator).

## 4.3  Proposal 3 for Rule 94

Proposal 3 was sponsored by William P. Adams, a former Commission employee and intervenor in this proceeding.  Adams’s proposal essentially mirrored Proposal 1 as to clearances between wireless antennas and power and communications conductors, and was similar to Proposal 2 in requiring that the antenna operator be responsible for powering down or shutting down a wireless antenna.  Proposal 3 was the only proposal addressing wireless antennas on the top of utility poles, although at hearing Adams recommended that pole-top provisions be deferred.  In his reply brief, Adams essentially withdrew Proposal 3 and instead supported Proposal 2.

# 5.  Disputed Provisions

The parties’ proposals differed on only a few provisions of the new Rule 94, and even those disputes were narrowed during evidentiary hearings.  Only the following issues were unresolved by the parties’ initial proposals:

- Should this proceeding consider making pole-top antenna requirements a part of Rule 94?

- Should Rule 94 provide a method of controlling or shutting down antennas?

- Should a wireless carrier be required to post signage providing information regarding compliance with the FCC’s maximum permissible exposure limits?

- Should a uniform six-foot vertical clearance level between antennas and supply conductors be expressly required?

- Should there be express exceptions for utility supply antennas and cable-embedded antennas?

# 6.  Pole-Top Antennas

Pole-top antennas are not addressed by the settlement agreement discussed below.  The GO 95/128 Rules Committee is currently evaluating proposed rules governing pole top installations.  We do not currently have a proposed rule before us on this issue.

ClearLinx urges the Commission to mandate that wireless antennas may be placed at the top of utility poles.  The Wireless Group does not advocate that the Commission adopt a specific rule now, but is concerned that the Rules Committee may not bring a consensus rule to the Commission.  The Wireless Group requests that the Commission establish an appropriate procedural mechanism so that a pole-top antenna rule is considered in a timely manner, whether or not the Rules Committee develops a consensus rule.  CPSD, IBEW, PG&E, and SDG&E disagree with both ClearLinx and the Wireless Group.  Instead these parties recommend that the Commission defer taking action until the issue has been thoroughly reviewed by the Rules Committee.

In the absence of a specific proposed rule, we will not adopt a construction rule for pole-top antennas at this time.  We encourage the members of the Rules Committee to make a good faith effort to achieve a statewide consensus on a proposed rule addressing pole-top antenna installations.

# 7.  Settlement Agreement

On August 23, 2006, 16 parties filed a settlement agreement in which the parties agreed to support a new Rule 94 that would be identical to Proposal 1, with the exception of two provisions (additional signage for antennas and methods of de-energizing antennas).  The settlement agreement resolves all disputed issues related to the two provisions in the proposed Rule 94, and requires signing parties to meet similar requirements via the settlement.  The proposed settlement is endorsed by virtually all parties, and no party opposes it.  This settlement agreement is attached to this decision as part of Appendix 1.

## 7.1  New Rule 94

The new Rule 94 endorsed by the settling parties is set forth in its entirety and attached to this decision as Appendix 1.  We note that the new Rule clearly defines antennas at issue; treats antennas as Class C equipment, thereby establishing many construction requirements; provides additional vertical clearances from other conductors and equipment; maintains vertical clearances from the ground; and requires a sign for each antenna installation marked with the contact information of the antenna operator.

### 7.1.1  Marking of an Antenna Operator’s Contact
          Information

The settlement agreement endorses marking requirements found in Proposal 1.  The marking requirements include the identity of the antenna operator, a 24-hour contact number for emergencies and information, and a unique identifier for the antenna installation.  George Lindsey, a PG&E lineman testifying on behalf of IBEW, explained that such contact information would be helpful to him as lineman, because he would be able to get more information about the antenna.  (Exhibit 9, at 3.)

Proposal 2, supported by SCE and the Wireless Group, did not contain this marking requirement.  However, at the evidentiary hearing on February 7, 2006, Nick Selby, appearing for Sprint Nextel, clarified that SCE and the Wireless Group do not oppose Rule 94.5 of Proposal 1.  Thereafter, no party opposed the Rule 94.5 marking requirement.

We find that this marking requirement will help ensure that linemen will be able to coordinate operations effectively with antenna operators.  We, therefore, conclude that it is appropriate to follow the recommendation of the settlement agreement and include a marking requirement in Rule 94.

### 7.1.2  Vertical Clearance Levels

The settlement agreement endorses clearance requirements found in Proposal 1.  Proposal 1 specifies a 6-foot vertical clearance requirement between antennas and supply conductors, including supporting elements of the equipment.

During evidentiary hearings, CPSD witness Fugere and three experienced linemen – Greg Walters of SDG&E, George Lindsey of IBEW, and PG&E witness Marc Brock – argued that a uniform 6-foot vertical clearance is needed.  Fugere testified that a wireless antenna with a vertical clearance of 4 feet or less from supply conductors would create a physical obstruction for one working on a pole and would expose the worker to potential electrical shock.  Walters cited a number of examples of when a 6-foot clearance would be necessary:  (1) when maneuvering with an 8-foot “hot stick” to apply temporary grounds on energized conductors from a safe distance; (2) when climbing on a pole with a complicated configuration of supply conductors; (3) when installing permanent primary jumpers to tie related electric circuits, and (4) when working with other linemen, each about 6 feet tall, on energized primary conductors.  In each case, Walters said, the pole worker “needs the 6 feet to be able to actually and comfortably and safely do his work.”  (Transcript, at 134.)  Lindsey and Brock similarly recommended a 6-foot vertical clearance, and maintained that anything substantially less would make it more likely that a lineman could come into contact with a supply conductor, causing an electric shock that could be fatal.

We conclude that the record evidence supports the settlement agreement’s endorsement of Proposal 1 clearance requirements.  Worker safety is our paramount concern.  The clearance requirements endorsed by the settlement agreement safeguard utility employees and provide clear guidance to antenna installers.  The new GO 95 rules, therefore, require these clearance levels.

### 7.1.3  Antenna Exceptions

The settlement agreement endorses antenna exceptions found in Proposal 1.  Proposal 1 stated that antennas utilized solely for the operation and maintenance of utility supply systems, along with strand-mounted antennas, would not be subject to the provisions of new Rule 94.

Significant record evidence supports these antenna exceptions.  Witnesses testified that supply antennas, such as SCADA antennas, are typically installed within the electric supply space of a distribution pole and, therefore, cannot meet the clearance requirements of Class C equipment.  Moreover, according to PG&E witness Brock, supply antennas do not raise the same RF exposure concerns of wireless antennas, since the RF exposure level from supply and cable-mounted antennas is usually less than the FCC’s general population/uncontrolled levels.  Electrical workers also have the ability to turn off the supply antenna’s power.  For these reasons, we conclude that it is appropriate follow the recommendation of the settlement agreement and exclude supply and strand-mounted antennas from the requirements of proposed Rule 94.

## 7.2  Marking and De-energizing Measures

The Rule 94 agreed to in the proposed settlement does not include Rule 94.6 (Identifying Exposure) and Rule 94.7 (Controlling Exposure) from Proposal 1.  However, the settlement provides that issues related to these proposed rules instead are addressed by private, voluntary agreement.  First, the settlement requires signatory antenna owners to provide further pole-mounted signage on joint use poles.  This signage describes compliance with the FCC exposure limits for each antenna installation and identifies the FCC’s recommended minimum approach distance.  Second, the settlement requires protocols for de-energizing antennas that emit RF energy in excess of the FCC’s General Population/Uncontrolled maximum exposure limits.  In the protocols for de-energizing antennas in non-emergency or routine situations, the antenna owner would be responsible for de-energizing an antenna upon request of any other utility or company with facilities attached to the affected pole.  In the protocols for de-energizing antennas in emergency situations, utility line crews would be authorized to de-energize the antenna if the antenna owner cannot be reached in time to deal with the emergency.

Parties assessed the impact of these settlement provisions at the evidentiary hearing on September 12, 2006.  In response to questions posed by the ALJ and assigned Commissioner, representatives of two union parties – IBEW and Communications Workers – stated that in their judgment the settlement provisions regarding additional signage and de-energizing antennas will provide the same level of protection for the line crews covered by the agreement as would Sections 94.6 and 94.7 of the original Proposal 1.  The advantage of the settlement, they said, was that these provisions could be put into place soon without the likelihood of jurisdictional challenge over state enforcement of these requirements.  The Commission’s CPSD, which was a principal author of the Proposal 1, stated that it supported the proposed settlement for much the same reasons as the unions, and it emphasized the importance of putting procedures in place to better protect line crews.

Questioned about enforceability of the settlement terms, counsel for the Wireless Group stated that any signatory party alleging breach of the settlement agreement can seek redress in civil courts or before this Commission, as appropriate.  Wireless Group counsel added that nothing in the agreement is intended to restrict the jurisdiction of the Commission.

Elements of the settlement agreement that are not contained in Rule 94 only apply to antennas installed on joint use utility poles.  Poles owned exclusively by PG&E and SCE are covered by licensing agreements that, according to those utilities, incorporate signage and de-energizing requirements consistent with the terms of the settlement agreement.

At the evidentiary hearing, SDG&E, which is not a signatory to the settlement agreement, explained that it has no jointly owned poles and antennas on its poles are governed by a licensing agreement.  SDG&E asserted that its licensing agreement imposes even more rigid restrictions than those provided for in the settlement.  The SDG&E license agreement requires a power shut-off device on site accessible to SDG&E line crews, and line crews are directed to work no less than 3 feet away from any RF-emitting antenna.  Counsel for SDG&E stated that the utility prefers to continue its licensing restrictions, but it nevertheless supports the settlement agreement in this proceeding.

## 7.3  Commission Review of the Settlement

We review this settlement under the Commission’s rules (Rule 12.1(d) of the Rules of Practice and Procedure).  Our inquiry examines whether the settlement is consistent with both the record and the law.

First, we find that the settlement is completely consistent with the record.  The settlement addresses the range of concerns and outcomes previously vetted by the parties and developed in the record.  Indeed, one of the primary concerns has been worker safety, and all union representatives expressed support for the settlement.  The settlement is comprehensive in addressing all the disputed issues to the satisfaction of the parties (even those who do not share poles).

Second, the settlement is consistent with the law.  By addressing the most contested features of these proposed regulations in private agreements among the affected parties, this decision removes the uncertainty of legal challenges to these rules, and allows these rules to become effective—and save lives—as soon as this decision is implemented.

In conclusion, our review of the settlement agreement convinces us that it should be approved.  We have examined the agreement pursuant to the Commission’s settlement rules, and we find that the settlement is reasonable in light of the whole record, consistent with law, and in the public interest.

# 8.  Additional Marking and De-energizing
     Safeguards

While the signatories to the settlement include the vast majority of joint pole owners and wireless carriers (except for SDG&E), we recognize that some antenna installations on poles under our jurisdiction may not be covered by the terms of the settlement agreement.  For example, we recognize that the settlement will not apply to some small electric utilities and small telephone utilities.  Similarly, an antenna owner or operator that is not a signatory to the settlement agreement will not be bound by terms of the settlement, and even a signatory utility will not be required by the settlement to replicate its terms with a non-party seeking to install an antenna.

In response to this incomplete coverage, our order today adopts additional rules that direct that no antenna owner or operator shall install an antenna on a joint use pole unless such installation is subject to an agreement with the pole owner(s) that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement approved herein.  The settlement agreement states, in relevant part:

1.  Markings Related to the FCC’s MPE Limits.

The Antenna Owner/Operator shall provide, and update as necessary, accurate information regarding compliance with the Federal Communications Commission’s Maximum Permissible Exposure (MPE) limits as set forth in Title 47 of the Code of Federal Regulations (CFR) for each particular Antenna installation.  The Antenna Owner/Operator shall communicate such information through the use of a pole mounted marking as described in Exhibit A  (Additional Marking Requirements) and in writing to the other utilities and/or companies with facilities affixed to the pole in accordance with Paragraph 4 of this Agreement.

2.  Means of De-energizing Antennas.

The Antenna Owner/Operator shall not install an Antenna on a joint use pole that emits RF energy in excess of the FCC’s General Population/ Uncontrolled maximum permissible exposure limits as set forth in 47 C.F.R. or effect a change to an existing Antenna site that will cause that Antenna to emit RF energy in excess of the FCC’s General Population/Uncontrolled maximum permissible exposure limits as set forth in 47 C.F.R. except by  providing to any other utility or company with facilities attached to the affected pole, a locally verifiable means to de-energize said Antenna.  The protocols set forth in Exhibit B shall apply to non-emergency or routine working conditions. The protocols set forth in Exhibit C shall apply to emergency working conditions.

3.  Exemption.

The provisions of this Agreement shall not apply to Antennas that are exempt from the provisions of General Order 95, Rule 94.

4.  Adoption of Operating Procedures.

The Settling Parties further agree to memorialize the agreements set forth in Section 1 and 2 of this Agreement (including the procedures and protocols to be adopted thereunder) in separate, private agreements with affected utilities, companies or municipalities or in the Northern California Joint Pole Association’s Operating Routine.  Such agreements and procedures shall be adopted in a timely manner and Settling Parties agree to execute any and all supplementary documents and take all actions which may be necessary or appropriate to give full force and effect to the terms and intent of this Agreement.

. . .

EXHIBIT A

ADDITIONAL MARKING REQUIREMENTS

Antenna Owner/Operators are responsible for the installation and upkeep of their sign or signs at each joint use site.

a.	In addition to the requirements of GO 95, Rule 94.5 (Marking), at a minimum, each Antenna Owner/Operator will also affix a sign that:

(i) identifies the applicable FCC exposure category (General Population/Uncontrolled or Occupational/Controlled);

(ii) identifies the FCC’s recommended minimum approach distance as set forth in 47 C.F.R.; and

(iii) is of weather and corrosion resistant material.

b.	The Antenna Owner/Operator will place the sign so that it is clearly visible to workers who otherwise climb the pole or ascend by mechanical means and affix said sign:

(i) no less than three (3) feet below the Antenna (measured from the top of the sign); and

(ii) no less than nine (9) feet above the ground line (measured from the bottom of the sign).

c.		The Antenna Owner/Operator may install a single sign that contains the information required by GO 95, Rule 94 and section (a) above, or separate signs. In the event one or more Antennas are affixed to a pole, each Antenna Owner/Operator shall provide a sign with sufficient information to allow workers to identify its Antennas.

EXHIBIT B

PROTOCOL FOR DE-ENERGIZING ANTENNAS IN NON-EMERGENCY OR ROUTINE WORKING CONDITIONS

In the event an Antenna subject to Section 2 needs to be de-energized to perform non-emergency work, e.g., routine maintenance and/or repairs, on a joint use distribution pole, the following shall apply:

  - The utility or company shall contact the Antenna Owner/Operator (in the case of a wireless carrier they shall contact the carrier’s Network Operations Center) with a minimum of twenty-four (24) hours advance notice.  The following information shall be provided:

i)   identity of the utility/company representative and call back number

ii)  the unique identifier of the Antenna

iii) the site address and/or location, if available

  - The Antenna Owner/Operator shall de-energize the Antenna at the requested time or at a time otherwise mutually agreed upon with the utility.

  - The procedures for de-energizing the subject Antenna shall provide the requesting utility or company with a satisfactory on-site means to verify the Antenna is de-energized.

  - Upon completion of the work on the site, the utility or company shall contact the Antenna Owner/Operator (in the case of a wireless carrier, its Network Operations Center shall be contacted) to inform them that the Antenna may be re-energized.

  - The Antenna shall not be re-energized by the Antenna Owner/Operator without confirmation from the utility or company.

  - The requesting utility or company will only re-energize the Antenna with the Antenna Owner/Operator’s prior written consent.

EXHIBIT C

PROTOCOL FOR DE-ENERGIZING ANTENNAS IN EMERGENCY WORKING CONDITIONS

In the event an Antenna subject to Section 2 needs to be de-energized in emergency working conditions, i.e., in a situation where there is an imminent or actual danger to public or worker safety necessitating immediate and non-routine work on the pole, for example in direct response to a fire, explosion, lightning, storm, earthquake, vehicular accident, terrorism, or some other unanticipated and catastrophic event, the following shall apply:

- The utility or company shall make a good faith effort to contact the Antenna Owner/Operator (in the case of a wireless carrier they shall contact the carrier’s Network Operations Center).   The following information shall be provided:

i)  identity of the utility/company representative and call back number

ii)  the unique identifier of the Antenna

iii) the site address and/or location, if available

iv) state nature of the emergency and/or site condition.

- The Antenna Owner/Operator shall de-energize the Antenna upon request in emergency working conditions.

- If the requesting utility or company is unable to contact the Antenna Owner/Operator, the requesting utility or company shall de-energize the subject antenna pursuant to mutually agreed upon procedures for that particular type of equipment or by using any necessary means available.  The procedures for de-energizing the subject Antenna referred to above shall provide the requesting utility or company with a satisfactory on-site means to de-energize the Antenna that is verifiable.

- Upon the completion of any necessary work to address the emergency, the utility or company  shall notify the Antenna Owner/Operator (in the case of a wireless carrier, its Network Operations Center shall be contacted) that all work has been completed so that the Antenna Owner/Operator can take any necessary actions to re-energize the site.

- The Antenna shall not be re-energized by the Antenna Owner/Operator without confirmation from the utility or company.

- The requesting utility or company will only re-energize the Antenna with the Antenna Owner/Operator’s prior written consent.”

These measures ensure that all utility linemen in California will benefit from the protections established in the settlement.  Antenna owners or operators not covered by the settlement agreement may file an advice letter with the Commission to ensure that its antenna installation(s) are subject to an agreement that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement.

The importance of uniformity in safety standards is reiterated in the record.  Testifying on behalf of CPSD, Raymond Fugere explained that “[t]o ensure worker safety, there’s a need for a statewide requirement to provide uniformity for construction of wireless antennas on jointly used poles.”  Marc Brock, testifying on behalf of PG&E, concurred that “there is a need for uniform construction standards for antenna installations.  This is needed for worker safety, public safety and system reliability.”

# 9.  Implementation of Rule Changes

The effective date for implementation of Rule 94 shall be no later than 180 days after issuance of the final decision in this proceeding.  The adoption of the Rule 94 will require utilities to change their company standards, communicate the changes to field personnel, and conduct varying degrees of training prior to full implementation of the rule.

Rule 94 is not retroactive.  It, therefore, does not affect wireless antennas already installed on utility poles through private agreements between antenna owners and joint pole operators.

# 10.  Comments on Alternate Proposed
       Decision

The alternate proposed decision of Commissioner Rachelle B. Chong was mailed to the parties on November 8, 2006 in accordance with Pub. Util. Code § 311(e) and Rule 14.1 of the Commission’s Rules of Practice and Procedure.  Opening comments on Commissioner Chong’s Alternate Proposed Decision were filed on November 28, 2006 by PG&E and SCE, jointly; SDG&E; and Cingular Wireless, Crown Castle USA, Inc., NextG Networks, Omnipoint Communications, Inc. dba T-Mobile, Sprint Nextel, and Verizon Wireless (Wireless Parties).  Reply comments were filed on December 5, 2006 by CCTA and ExteNet Systems, Inc. (ExteNet) (formerly ClearLinx Network Corporation).

In response to the comments, we have made several clarifications, corrections and changes to the alternate proposed decision.

PG&E and SCE filed comments in support of Commissioner Chong’s Alternate Proposed Decision.  SDG&E also expressed support for the approach taken in the decision.

The Wireless Parties support the core components of the alternate proposed decision.  However, the Wireless Parties do not support the annual reporting requirement in the decision, arguing that the reporting requirement infringes on the due process interests of parties because the parties were not provided notice that the Commission might impose reporting requirements.  The Wireless Parties also assert that the reporting requirement is inconsistent with the settlement agreement, which does not include reporting requirements.

We do not need to address the substance of the Wireless Parties’ arguments regarding the reporting requirement.  Our adoption of new GO 95 Rules moots the need for any reporting requirement.  The Rules ensure that all antenna installations will be subject to marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement.  It no longer is the case that some antennas may fail to be covered by the settlement agreement or terms at least as strict as those set forth in the settlement agreement.  Thus, we delete the previously proposed reporting requirement.

In Comments on the Alternate Proposed Decision of Commissioner Brown, the Wireless Parties committed to abide by the terms of the settlement agreement with respect to any antenna placed on any jointly owned or used pole, whether or not the pole owner or other pole users are parties to the settlement.  We have added a reference to that commitment in the discussion above.

The Wireless Parties also request clarifying language related to pole-top attachments, noting that the Wireless Parties previously asked the Commission to monitor the Rules Committee’s efforts.  ExteNet echoed the same concern.

We have modified the discussion to more accurately characterize the positions of parties.

The Wireless Parties also state that the decision need not find that the provisions of the settlement are supported by “substantial record evidence.”  They specifically cite the antenna exceptions contained in the agreement as an issue the Wireless Parties disputed during the proceeding, but consented to in the context of the settlement.  CCTA disagrees with the Wireless Parties on this point.  CCTA points out that in approving the settlement, the Commission is adopting a Rule 94 which stands independent of the settlement and applies to parties that did not participate in the settlement.  Therefore, making findings specific to the new Rule 94 is appropriate.

We agree with CCTA.  Since the Rule 94 endorsed by the settling parties will apply to non-settling parties, it is appropriate for the Commission to make findings relative to each element of the Rule 94 that we adopt.

In addition to revisions made in response to comments, we have made other minor corrections and clarifications to the proposed decision.

# 10.  Assignment of Proceeding

Geoffrey F. Brown is the assigned Commissioner and Glen Walker is the Assigned ALJ in this proceeding.

Findings of Fact

- GO 95 governs the construction of overhead electrical supply and communications systems.

- GO 95 currently does not contain specific rules for the installation of wireless antennas on utility poles.

- Commission staff, industry representatives, labor representatives, and other members of the public participated in seven days of public workshops devoted to developing a proposed new Rule 94 concerning wireless antennas.

- On September 12, 2005, the parties submitted a joint workshop report that included three alternative proposals for a new Rule 94 that would establish uniform construction standards for the attachment of wireless antennas to jointly used utility poles.

- Proposal 1 for Rule 94 was sponsored by CPSD, IBEW, Communications Workers, PG&E, and SDG&E.

- Proposal 2 for Rule 94 was sponsored by SCE and was supported by Crown Castle USA, Inc.; Cingular Wireless; NextG Networks; Sprint Nextel; Omnipoint Communications, Inc. dba T-Mobile; Verizon Wireless; and intervenor William Adams.

- Proposal 3 for Rule 94 was sponsored by William Adams, but later was withdrawn.

- On February 24, 2005, the Commission issued an OIR that proposed revisions to GO 95 that would establish uniform construction standards for attaching wireless antennas to jointly used poles and towers.

- On July 18, 2006, parties, pursuant to Rule 84 of the Rules of Practice and Procedure, filed a joint petition to allow them to pursue settlement discussions.

- The joint petition was granted on July 20, 2006.

- On July 28, 2006, PG&E provided notice of a conference regarding a proposed settlement of the disputed issues in this proceeding, and the conference was held on August 4, 2006.

- An unopposed settlement agreement by the parties was presented to the Commission on August 23, 2006.

- The settlement agreement was signed by CPSD; IBEW; Communications Workers; PG&E; AT&T California; CCTA; Clearlinx Network Corporation; Crown Castle USA, Inc.; New Cingular Wireless PCS, LLC; NextG Networks of California Inc.; Omnipoint Communications, Inc., dba T-Mobile; Southern California Edison Company; Sprint Nextel; Verizon California Inc.; Verizon Wireless; and William Adams.

- The settling parties agreed to support a new Rule 94 that would be identical to Proposal 1, with the exception of Rule 94.6 and Rule 94.7.  All other disputed issues relating to Rule 94 were resolved to the satisfaction of all signing parties through private agreements between signatory utilities and antenna owners.

- The Rule 94 agreed to in the settlement would clearly define antennas; treat antennas as Class C equipment, thereby establishing many construction requirements; provide additional vertical clearances from other conductors and equipment; maintain vertical clearances from the ground; and require a sign for each antenna installation marked with the contact information of the antenna operator.

- A marking requirement consisting of the identity of the antenna operator, a 24-hour contact number for emergencies and information, and a unique identifier for the antenna installation will help linemen coordinate operations with antenna operators.

- A vertical clearance between a supply conductor and antenna of less than six feet could create a physical obstruction for workers.

- A uniform six foot vertical clearance requirement would safeguard utility employees and provide clear guidance to antenna installers.

- SCADA antennas typically are installed within the electric supply space of a distribution pole.

- Electric workers have the ability to turn off the power to SCADA antennas.

- The settlement agreement requires signatory antenna owners to provide additional pole mounted signage on joint use utility poles.  This signage must describe compliance with the FCC exposure limits for each antenna installation and identify the FCC’s recommended minimum approach distance.

- The settlement agreement requires protocols for de-energizing antennas that emit RF energy in excess of the FCC’s General Population/Uncontrolled maximum exposure limits.

- The settlement provides safeguards for line crews working on utility poles.

- Utility employees are safeguarded by requiring antenna installations to be subject an agreement with the pole owner(s) that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement.

- Public and utility employee safety requires that the provisions of Rule 94, as set forth in Appendix 1, be adopted as part of GO 95.

Conclusions of Law

- The Public Utilities Code establishes that safety issues may be subject to Commission regulation.

- Markings that consist of the identity of the antenna operator, a 24-hour contact number for emergencies and information, and a unique identifier for the antenna installation should be required.

- It is reasonable to require that antenna installations are subject to an agreement with the pole owner(s) that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement adopted herein.  Antenna owners or operators not covered by the settlement agreement may file an advice letter with the Commission to ensure its antenna installation(s) are subject to an agreement that includes marking and de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in the settlement agreement.

- A six-foot vertical clearance requirement should be adopted to protect workers from electric shock.

- It is reasonable to exclude supply and strand-mounted antennas from the requirements of proposed Rule 94.

- Rule 94 as set forth in Appendix 1 of this decision should be approved and adopted, because public and utility employee safety so requires.

- The settlement agreement set forth in Appendix 1 of this decision should be approved, because it is reasonable in light of the whole record, consistent with law, and in the public interest.

- Rule 94 should become effective prospectively 180 days after issuance of the final decision in this proceeding.

ORDER

IT IS ORDERED that:

- General Order (GO) 95 is amended to incorporate Rule 94 and the amendment to Rule 20.0, as set forth in Appendix 1 attached hereto and made part hereof.

- The revisions to GO 95 authorized today will become effective prospectively 180 days after the date of today’s decision.

- The settlement agreement is approved and attached as reference to GO 95 as Appendix H of GO 95.

- Rulemaking 05-02-023 is closed.

This order is effective today.

Dated February 15, 2007, at San Francisco, California.

MICHAEL R. PEEVEY

President

DIAN M. GRUENEICH

JOHN A. BOHN

RACHELLE B. CHONG

Commissioners

APPENDIX 1

New GO 95, Rule 20 (Definition)

20.0	Antenna means a device for emitting and/or receiving radio frequency signals.

New GO 95, Rule 94 – Antennas

94	Antennas

94.1	Definition (See Rule 20.0)

94.2	Maintenance and Inspection (See Rules 31.1 and 31.2)

94.3	General Requirements

On joint use poles supporting Class T, C, L or H Circuits (up to 50 kV), the following shall apply:

A.	Antennas shall meet the requirements of Class C equipment, unless otherwise specified in this rule.

B.	All associated elements of the antenna (e.g. associated cables, messengers, and pole line hardware) shall meet the requirements of Class C circuits.

94.4	Clearances

A.	Antennas and supporting elements (e.g. crossarms, brackets) shall maintain a vertical clearance of 6 feet from Supply Conductors operating at 0 – 50kV.  (See Figure 94-1)

B.	Antennas and supporting elements (e.g. crossarms, brackets) shall maintain a 2 ft. vertical separation from communication conductors and equipment.  (See Figure 94-2)

C.	Antennas shall maintain a 2 ft. horizontal clearance from centerline of pole.  (See Figures 94-1 and 94-2)

D.	Antennas shall have a vertical clearance above ground as specified in Table 1, Column B, Cases 1 to 6a.

94.5	Marking

A.	No antenna owner or operator shall install an antenna on a joint use pole unless such installation is subject to an agreement with the pole owner(s) that includes marking requirements that are substantially similar to and achieve at least the same safety standards as those set forth in Appendix H to GO 95.

B.	Joint use poles shall be marked with a sign for each antenna installation as follows:

(1)	Identification of the antenna operator

(2)	A 24-hour contact number of antenna operator for Emergency or Information

(3)	Unique identifier of the antenna installation.

  - De-energizing

No antenna owner or operator shall install an antenna on a joint use pole unless such installation is subject to an agreement with the pole owner(s) that includes de-energizing protocols that are substantially similar to and achieve at least the same safety standards as those set forth in Appendix H to GO 95.

Exceptions:

Antennas utilized by utilities for the sole purpose of operating and monitoring their supply system are exempt from this rule and shall only meet the construction and clearance requirements of supply equipment.

Antennas embedded in or attached to communication cables and messengers are exempt from this rule and shall only meet the construction requirements for Class C circuits.

Appendix H to GO 95

SETTLEMENT AGREEMENT AMONG AT&T CALIFORNIA, CALIFORNIA CABLE & TELECOMMUNICATIONS ASSOCIATION, CLEARLINX NETWORK CORPORATION, COMMUNICATIONS WORKERS OF AMERICA DISTRICT 9, CONSUMER PROTECTION AND SAFETY DIVISION, CROWN CASTLE USA INC., INTERNATIONAL BROTHERHOOD OF ELECTRICAL WORKERS LOCAL 1245,  NEW CINGULAR WIRELESS PCS, LLC, NEXTG NETWORKS OF CALIFORNIA INC., OMNIPOINT COMMUNICATIONS, INC., dba T-MOBILE, PACIFIC GAS AND ELECTRIC COMPANY, SOUTHERN CALIFORNIA EDISON COMPANY,  SPRINT NEXTEL, VERIZON CALIFORNIA INC., VERIZON WIRELESS AND WILLIAM ADAMS

In accordance with Rule 51.1 of the California Public Utilities Commission’s (Commission) Rules of Practice and Procedure, AT&T California, California Cable & Telecommunications Association, Clearlinx Network Corporation, Communications Workers of America District 9, Consumer Protection and Safety Division, Crown Castle USA, Inc., International Brotherhood of Electrical Workers Local 1245, New Cingular Wireless PCS, LLC, NextG Networks of California Inc., Omnipoint Communications, Inc., dba T-Mobile, Pacific Gas and Electric Company, Southern California Edison Company,  Sprint Nextel, Verizon California Inc., Verizon Wireless and William Adams (collectively, the “Settling Parties”) hereby enter into this Settlement Agreement (Agreement) to resolve all issues among the Settling Parties in Rulemaking (R.) 05-02-023, Order Investigation Rulemaking to consider uniform rules for attaching wireless antennas to jointly used poles.

RECITALS

- On February 24, 2005, the Commission issued an Order Instituting Rulemaking in R.05-02-023 to consider a new rule to GO 95 to establish uniform construction standards for attaching wireless antennas to jointly used utility poles.

- Evidentiary hearings were conducted in the proceeding on February 7-9, 2006,

during which the Commission heard testimony from nine witnesses and received 22 exhibits into evidence.

- Opening and reply briefs were filed on March 13 and 28, 2006, respectively, at which time the matter was submitted for Commission decision.

- On April 25, 2006, the Assigned Administrative Law Judge, ALJ Walker, issued his Proposed Decision (“the PD”).  Opening and Reply Comments on the PD were filed on May 15 and 22, 2006, respectively.  ALJ Walker has issued two revised versions of his Proposed Decision, which adopted Proposal 1 in its entirety, including the provisions of Rule 94.6 and 94.7.

- On July 18, 2006, several parties in the proceeding submitted a joint petition to set aside submission of the proceeding pursuant to Rule 84 of the Commission’s Rules of Practice and Procedure.   The petition requested the Commission set aside the submission of the proceeding temporarily to allow the parties to pursue settlement discussions.   On July 20, 2006, Assigned Commissioner Geoffrey F. Brown and Administrative Law Judge Michelle Cooke ruled that the parties shall submit any settlement on or before August 10, 2006.

- Pursuant to Rule 51.1(b) of the Commission’s Rules of Practice and Procedure, on July 28, 2006, the Settling Parties served notice of a settlement conference to be held telephonically on August 4, 2006.

- On August 4, 2006, the settlement conference was held as scheduled.  Following the settlement conference, the Settling Parties continued settlement discussions, resulting in this Agreement.

SETTLEMENT AGREEMENT

In order to resolve disputed issues of fact and law and settle on a mutually acceptable outcome to the proceeding with due regard for public and worker safety concerns, and subject to the Recitals and reservations set forth in this Agreement, the Settling Parties hereby agree that this Agreement resolves all disputed issues relating to Rule 94.6 and Rule 94.7 raised in this proceeding.

The Agreement is presented to the Commission pursuant to Rule 51 of the Commission’s Rules of Practice and Procedure.

The Settling Parties agree that, in the event any party, as a joint owner, lessee or licensee (“Antenna Owner/Operator”) seeks to install or causes the installation of an Antenna (as defined in General Order (GO) 95 Rule 20.0) on a joint use utility pole, it is agreed that:

- Markings Related to the FCC’s MPE Limits.

The Antenna Owner/Operator shall provide, and update as necessary, accurate information regarding compliance with the Federal Communications Commission’s Maximum Permissible Exposure (MPE) limits as set forth in Title 47 of the Code of Federal Regulations (CFR) for each particular Antenna installation.  The Antenna Owner/Operator shall communicate such information through the use of a pole mounted marking as described in Exhibit A

(Additional Marking Requirements) and in writing to the other utilities and/or companies with facilities affixed to the pole in accordance with Paragraph 4 of this Agreement.

- Means of De-energizing Antennas.

The Antenna Owner/Operator shall not install an Antenna on a joint use pole that emits RF energy in excess of the FCC’s General Population/Uncontrolled maximum permissible exposure limits as set forth in 47 C.F.R. or effect a change to an existing Antenna site that will cause that Antenna to emit RF energy in excess of the FCC’s General Population/Uncontrolled maximum permissible exposure limits as set forth in 47 C.F.R.  except by  providing to any other utility or company with facilities attached to the affected pole, a locally verifiable means to de-energize said Antenna.  The protocols set forth in Exhibit B shall apply to non-emergency or routine working conditions.  The protocols set forth in Exhibit C shall apply to emergency working conditions.

3.	Exemption.

The provisions of this Agreement shall not apply to Antennas that are exempt from the provisions of General Order 95, Rule 94.

4.	Adoption of Operating Procedures.

The Settling Parties further agree to memorialize the agreements set forth in Section 1 and 2 of this Agreement (including the procedures and protocols to be adopted thereunder)  in separate, private agreements with affected utilities, companies or municipalities or in the Northern California Joint Pole Association’s Operating Routine.  Such agreements and procedures shall be adopted in a timely manner and Settling Parties agree to execute any and all supplementary documents and take all actions which may be necessary or appropriate to give full force and effect to the terms and intent of this Agreement.

- Commission Approval of Settlement and Modification of Rule 94.

The Settling Parties shall jointly request Commission approval of this Agreement and that the Commission adopt Rule 94, as that rule is set forth in Exhibit 1 of the Proposed Decision of ALJ Walker (mailed April 25, 2006), with the exception of provisions 94.6 and 94.7, which the parties stipulate should be removed from the rule.  The Settling Parties additionally agree to actively support prompt approval of the Agreement and adoption of the modified Rule 94.  Active support may include briefing, comments on the proposed decision, written and oral testimony, if testimony is required, appearance at hearings, and other means as needed to obtain the approvals sought.  The Settling Parties further agree to participate jointly in briefings to Commissioners and their advisors, either in-person or by telephone, as needed regarding the Agreement and the issues compromised and resolved by it.

- This Agreement is contingent upon (1) the Commission approving the terms and conditions herein as reasonable, and adopting it unconditionally and without modification, and (2) the Commission adopting the modified Rule 94 as provided in Paragraph 5, above.    Upon satisfaction of these contingencies, the Settling Parties agree to waive any and all rights to challenge and/or appeal in any state or federal forum the Commission’s decision in this proceeding.

- The Settling Parties agree to negotiate in good faith to resolve any dispute arising out of the implementation, interpretation or alleged breach of this Agreement.   In the event such negotiations are unsuccessful, the Settling Parties may seek appropriate relief from the Commission.  Such proceeding before the Commission will be limited to determining whether there has been a breach of this Agreement and ordering appropriate relief.   In the event any of the Settling Parties do not reach agreement on the protocols described in this Agreement, the Commission may mediate a resolution between those Settling Parties.    Nothing herein is intended to expand or restrict the jurisdiction of the Commission and the Settling Parties retain all of their rights with respect thereto.

- The Settling Parties agree that this Agreement represents a compromise of positions, without agreement or endorsement of disputed facts and law presented by the Settling Parties in the proceeding.

- This Agreement and the covenants and agreements contained herein shall be binding on, and inure to the benefit of, the parties hereto and their respective heirs, successors and assigns.   The Settling Parties further agree and acknowledge that this Agreement and the covenants and agreements contained herein shall remain binding on the Settling Parties, notwithstanding the expiration of the term of any contract, lease or license relating to the use of a joint use pole.

- This Agreement embodies the entire understanding and agreement of the Settling Parties with respect to the matters described herein, and, except as described herein, supersedes and cancels any and all prior oral or written agreements, principles, negotiations, statements, representations or understandings among the Settling Parties relating to the use of joint use poles.

- The Settling Parties have bargained earnestly and in good faith to achieve this Agreement.  The Settling Parties intend the Agreement to be interpreted and treated as a unified, interrelated agreement.

- Each of the Settling Parties hereto and their respective counsel and advocates have contributed to the preparation of this Agreement.  Accordingly, the Settling Parties agree that no provision of this Agreement shall be construed against any Party because that Party or its counsel or advocate drafted the provision.

- Each of the Settling Parties represents that it is duly authorized to enter into this Agreement, and each person signing on behalf of an entity represents that he or she is duly authorized to sign on behalf of that entity.

- This document may be executed in counterparts, each of which shall be deemed an original, but all of which together shall constitute one and the same instrument.

- This Agreement shall become effective among the Settling Parties on the date the last Party executes the Agreement as indicated below.

- In witness whereof, intending to be legally bound, the Settling Parties hereto have duly executed this Agreement on behalf of the Settling Parties they represent:

AT&T California

By:

Its:

California Cable & Telecommunications Association

By:

Its:

Clearlinx Network Corporation

By:

Its:

Communications Workers of America District 9

By:

Its:

Consumer Protection and Safety Division

By:

Its:

Crown Castle USA Inc.

By:

Its:

International Brotherhood of Electrical Workers Local 1245

By:

Its:

New Cingular Wireless PCS, LLC

By:

Its:

NextG Networks of California, Inc.

By:

Its:

Omnipoint Communications, Inc., dba T-Mobile

By:

Its:

Pacific Gas and Electric Company

By:

Its:

Southern California Edison Company

By:

Its:

Sprint Nextel

By:

Its:

Verizon California Inc.

By:

Its:

Verizon Wireless

By:

Its:

William Adams

By:

EXHIBIT A

ADDITIONAL MARKING REQUIREMENTS

Antenna Owner/Operators are responsible for the installation and upkeep of their sign or signs at each joint use site.

a.	In addition to the requirements of GO 95, Rule 94.5 (Marking), at a minimum, each Antenna Owner/Operator will also affix a sign that:

(i) identifies the applicable FCC exposure category (General Population/Uncontrolled or Occupational/Controlled);

(ii) identifies the FCC’s recommended minimum approach distance as set forth in 47 C.F.R.; and

(iii) is of weather and corrosion resistant material.

b.	The Antenna Owner/Operator will place the sign so that it is clearly visible to workers who otherwise climb the pole or ascend by mechanical means and affix said sign:

(i) no less than three (3) feet below the Antenna (measured from the top of the sign); and

(ii) no less than nine (9) feet above the ground line (measured from the bottom of the sign).

c.		The Antenna Owner/Operator may install a single sign that contains the information required by GO 95, Rule 94 and section (a) above, or separate signs. In the event one or more Antennas are affixed to a pole, each Antenna Owner/Operator shall provide a sign with sufficient information to allow workers to identify its Antennas.

EXHIBIT B

PROTOCOL FOR DE-ENERGIZING ANTENNAS IN NON-EMERGENCY OR ROUTINE WORKING CONDITIONS

In the event an Antenna subject to Section 2 needs to be de-energized to perform non-emergency work, e.g., routine maintenance and/or repairs, on a joint use distribution pole, the following shall apply:

a.	The utility or company shall contact the Antenna Owner/Operator (in the case of a wireless carrier they shall contact the carrier’s Network Operations Center) with a minimum of twenty-four (24) hours advance notice.  The following information shall be provided:

i)   identity of the utility/company representative and call back number

ii)  the unique identifier of the Antenna

iii) the site address and/or location, if available

b.	The Antenna Owner/Operator shall de-energize the Antenna at the requested time or at a time otherwise mutually agreed upon with the utility.

c.	The procedures for de-energizing the subject Antenna shall provide the requesting utility or company with a satisfactory on-site means to verify the Antenna is de-energized.

d.	Upon completion of the work on the site, the utility or company shall contact the Antenna Owner/Operator (in the case of a wireless carrier, its Network Operations Center shall be contacted) to inform them that the Antenna may be re-energized.

e.	The Antenna shall not be re-energized by the Antenna Owner/Operator without confirmation from the utility or company.

f.	The requesting utility or company will only re-energize the Antenna with the Antenna Owner/Operator’s prior written consent.

EXHIBIT C

PROTOCOL FOR DE-ENERGIZING ANTENNAS IN EMERGENCY WORKING CONDITIONS

In the event an Antenna subject to Section 2 needs to be de-energized in emergency working conditions, i.e., in a situation where there is an imminent or actual danger to public or worker safety necessitating immediate and non-routine work on the pole, for example in direct response to a fire, explosion, lightning, storm, earthquake, vehicular accident, terrorism, or some other unanticipated and catastrophic event, the following shall apply:

a.	The utility or company shall make a good faith effort to contact the Antenna Owner/Operator (in the case of a wireless carrier they shall contact the carrier’s Network Operations Center).   The following information shall be provided:

i)  identity of the utility/company representative and call back number

ii)  the unique identifier of the Antenna

iii) the site address and/or location, if available

iv) state nature of the emergency and/or site condition.

b.	The Antenna Owner/Operator shall de-energize the Antenna upon request in emergency working conditions.

c.	If the requesting utility or company is unable to contact the Antenna Owner/Operator, the requesting utility or company shall de-energize the subject antenna pursuant to mutually agreed upon procedures for that particular type of equipment or by using any necessary means available.  The procedures for de-energizing the subject Antenna referred to above shall provide the requesting utility or company with a satisfactory on-site means to de-energize the Antenna that is verifiable.

d.	Upon the completion of any necessary work to address the emergency, the utility or company  shall notify the Antenna Owner/Operator (in the case of a wireless carrier, its Network Operations Center shall be contacted) that all work has been completed so that the Antenna Owner/Operator can take any necessary actions to re-energize the site.

e.	The Antenna shall not be re-energized by the Antenna Owner/Operator without confirmation from the utility or company.

f.	The requesting utility or company will only re-energize the Antenna with the Antenna Owner/Operator’s prior written consent.

(END OF APPENDIX 1)

APPENDIX A

| ************ APPEARANCES ************ William P. Adams ADAMS ELECTRICAL SAFETY CONSULTING 716 BRETT AVENUE ROHNERT PARK CA 94928-4012 (707) 795-7549 For: Self Bruce Mclaughlin BRAUN & BLAISING, P.C. 915 L STREET, SUITE 1420 SACRAMENTO CA 95814 (916) 326-5812 mclaughlin@braunlegal.com For: California Municipal Utilities Association (CMUA) Maria L. Bondonno Legal Division RM. 4008 505 VAN NESS AVE San Francisco CA 94102 3298 (415) 355-5594 bon@cpuc.ca.gov Maria Politzer CALIFORNIA CABLE & TELECOM ASSOCIATION 360 22ND STREET, NO. 750 OAKLAND CA 94612 (510) 628-8043 126 mp@calcable.org For: CCTA Jerome F. Candelaria CALIFORNIA CABLE TELEVISION ASSOCIATION 360 22ND STREET, NO. 750 OAKLAND CA 94612 (510) 628-8043 jfc@calcable.org For: California Cable Television Association John C. Dodge Attorney At Law COLE, RAYWID & BRAVERMAN, LLP 1919 PENNSYLVANIA AVE., N.W., STE 200 WASHINGTON DC 20006 (202) 828-9805 jdodge@crblaw.com For: Crown Castle | Robert L. Ritter Attorney CROWN CASTLE INTERNATIONAL 2000 CORPORATE DRIVE CANONSBURG PA 15317 (724) 416-2417 bob.ritter@crowncastle.com For: Crown Castle James W. Mc Tarnaghan Attorney At Law DUANE MORRIS LLP ONE MARKET, SPEAR TOWER 2000 SAN FRANCISCO CA 94105-1104 (415) 957-3088 jwmctarnaghan@duanemorris.com For: Verizon Wireless Landis Martilla IBEW LOCAL 1245 30 ORANGE TREE CIRCLE VACAVILLE CA 95687 (415) 469-9903 lkm4@ibew1245.com Anita Taff-Rice Attorney At Law LAW OFFICES OF ANITA TAFF-RICE 1547 PALOS VERDES MALL, NO. 298 WALNUT CREEK CA 94597 (415) 699-7885 anitataffrice@earthlink.net For: Clearlinx Earl Nicholas Selby Attorney At Law LAW OFFICES OF EARL NICHOLAS SELBY 418 FLORENCE STREET PALO ALTO CA 94301 (650) 323-0990 ens@loens.com For: Nextel of California, Inc./Sprint Nextel Corporation Shanise Black Deputy City Attorney LOS ANGELES DEPARTMENT OF WATER & POWERA 111 NORTH HOPE STREET, ROOM 340 LOS ANGELES CA 90012 (213) 367-4520 Shanise.Black@ladwp.com For: Los Angeles Department of Water & Power |
| --- | --- |
| Barry F. Mc Carthy C. SUSIE BERLIN Attorney At Law MC CARTHY & BERLIN 100 PARK CENTER PLAZA,SUITE 501 SAN JOSE CA 95113 (408) 288-2080 bmcc@mccarthylaw.com For: City of Anaheim; Northern California Power Agency; Turlock Irrigation District Barry F. Mccarthy C. SUSIE BERLIN Attorney At Law MCCARTHY & BERLIN, LLP 100 PARK CENTER PLAZA, SUITE 501 SAN JOSE CA 95113 (408) 288-2080 bmcc@mccarthylaw.com For: City of Anaheim, Northern California Power Agency, Turlock Irrigation District Nicole Mason NEXT G NETWORKS OF CALIFORNIA, INC. 2216 OTOOLE AVE. SAN JOSE CA 95131-1326 (408) 719-8510 nmason@nextgnetworks.net For: NextG Networks of California, Inc. Norine Luker NEXT G NETWORKS OF CALIFORNIA, INC. 2216 OTOOLE AVE SAN JOSE CA 95131-1326 (408) 719-8510 X 185 nluker@nextgnetworks.net Robert L. Delsman Attorney At Law NEXTG NETWORKS OF CALIFORNIA, INC. 2216 O TOOLE AVENUE SAN JOSE CA 95131 rdelsman@nextgnetworks.net For: NextG Networks of California, Inc. Patrick J. Geoffrey PACIFIC GAS & ELECTRIC COMPANY 123 MISSION STREET SAN FRANCISCO CA 94105 (415) 973-8096 pjg3@pge.com For: Pacific Gas & Electric Company | Grant Guerra PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, ROOM 3103 SAN FRANCISCO CA 94105 (415) 973-3728 gxgw@pge.com For: Pacific Gas and Electric Company Steven Cohn Chief General Counsel SACRAMENTO MUNICIPAL UTILITY DISTRICT 6201 S STREET, M.S.B406 PO BOX 15830 SACRAMENTO CA 95852-1830 (916) 732-6121 scohn@smud.org Charles Manzuk SAN DIEGO GAS & ELECTRIC 8330 CENTURY PARK COURT, CP 32D SAN DIEGO CA 92123 (858) 636-5548 cmanzuk@semprautilities.com For: SAN DIEGO GAS & ELECTRIC Celeste Easton Attorney At Law SAN DIEGO GAS & ELECTRIC COMPANY 555 WEST FIFTH STREET, STE. 1400 LOS ANGELES CA 90013 (213) 244-2942 Ceaston@sempra.com For: San Diego Gas & Electric Gregory L. Walters SAN DIEGO GAS & ELECTRIC COMPANY 8316 CENTURY PARK COURT SAN DIEGO CA 92123 (858) 654-8396 gwalters@semprautilities.com For: San Diego Gas & Electric Lori Ortenstone Attorney At Law SBC R00M 1300 101 W. BROADWAY SAN DIEGO CA 92101 (619) 237-3329 lori.ortenstone@att.com For: SBC California |
| Aimee M. Smith Attorney At Law SEMPRA ENERGY 101 ASH STREET HQ13 SAN DIEGO CA 92101 (619) 699-5042 amsmith@sempra.com For: San Diego Gas & Electric Company Danielle Padula SOUTHERN CALIFORNIA EDISON 2244 WALNUT GROVE AVENUE ROSEMEAD CA 91770 (626) 302-6932 danielle.padula@sce.com For: Southern California Edison Stephen H. Kukta Counsel SPRINT NEXTEL CORP. 201 MISSION STREET, SUITE 1400 SAN FRANCISCO CA 94105 (415) 572-8358 stephen.h.kukta@sprint.com For: Sprint Nextel Corp. Suzanne Toller LEON BLOOMFIELD T-MOBILE 1755 CREEKSIDE OAKS DRIVE, STE. 190 SACRAMENTO CA 95833 (916) 643-8926 susan.lipper@t-mobile.com For: T-Mobile USA, Inc. Paul P. Strange Attorney At Law THE STRANGE LAW FIRM 282 SECOND STREET, SUITE 201 SAN FRANCISCO CA 94105 (415) 243-3200 strange@strangelaw.net For: SBC California (AT&T California) Jesus G. Roman VERIZON CALIFORNIA, INC. 112 S. LAKEVIEW CANYON ROAD, CA501LB THOUSAND OAKS CA 91362 (805) 372-6233 jesus.g.roman@verizon.com | Edward R. Mcgah, Jr. Attorney At Law VERIZON WIRELESS 15505 SAND CANYON AVENUE IRVINE CA 92618 (949) 286-8181 Edward.McGah@verizonwireless.com For: Verizon Wireless Bryan N. Tramont WILKINSON BARKER KNAUER, LLP 2300 N. STREET, NW, SUITE 700 WASHINGTON DC 20037-1128 (202) 783-4141 btramont@wbklaw.com For: Verizon Wireless Leon M. Bloomfield Attorney At Law WILSON & BLOOMFIELD LLP 1901 HARRISON STREET, SUITE 1620 OAKLAND CA 94612 (510) 625-8250 lmb@wblaw.net For: Wireless Group-Cingular, Crown Castle, NextG Networks of California, Sprint, T-Mobile & Verizon Wireless ********** STATE EMPLOYEE *********** Andrew Campbell Executive Division RM. 5304 505 VAN NESS AVE San Francisco CA 94102 3298 (415) 703-2501 agc@cpuc.ca.gov Richard Clark Consumer Protection & Safety Division RM. 2205 505 VAN NESS AVE San Francisco CA 94102 3298 (415) 703-2349 rwc@cpuc.ca.gov Raymond G. Fugere Consumer Protection & Safety Division RM. 500 320 WEST 4TH STREET SUITE 500 Los Angeles CA 90013 (213) 576-7015 rgf@cpuc.ca.gov |
| Peter Hanson Executive Division RM. 4104 505 VAN NESS AVE San Francisco CA 94102 3298 (415) 703-1053 pgh@cpuc.ca.gov Raffy Stepanian Consumer Protection & Safety Division RM. 500 320 WEST 4TH STREET SUITE 500 Los Angeles CA 90013 (213) 576-7019 rst@cpuc.ca.gov Glen Walker Administrative Law Judge Division RM. 5106 505 VAN NESS AVE San Francisco CA 94102 3298 (415) 703-1232 gew@cpuc.ca.gov ********* INFORMATION ONLY ********** Sarah Beserra 39 CASTLE HILL COURT VALLEJO CA 94591 sbeserra@napanet.net Margaret Felts President CALIFORNIA COMMUNICATIONS ASSN 1851 HERITAGE LANE STE 255 SACRAMENTO CA 95815-4923 (916) 567-6700 mcf@calcomwebsite.com CALIFORNIA ENERGY MARKETS 517-B POTRERO AVENUE SAN FRANCISCO CA 94110 (415) 552-1764 X 17 cem@newsdata.com Cindy Manheim CINGULAR WIRELESS PO BOX 97061 REDMOND WA 98073-9761 (425) 580-8112 cindy.manheim@cingular.com For: Cingular Wireless | George Granger V.P. External Affairs CINGULAR WIRELESS 4420 ROSEWOOD DRIVE, 4TH FLOOR PLEASANTON CA 94588 (925) 227-3070 george.granger@cingular.com For: Cingular Wireless Alison Kott Deputy City Attorney CITY OF ANAHEIM 200 S. ANAHEIM BLVD., SUITE 356 ANAHEIM CA 92805 (714) 765-5169 akott@anaheim.net For: CITY OF ANAHEIM David Hurlburt Safety Committee Chair COMMUNICATION WORKERS OF AMERICA 9410 240 - 2ND ST. SAN FRANCISCO CA 94105 (415) 777-9410 dghurlb@pacbell.net For: Local 9410 Communication Workers of America Holly Ernst Groschner Vice President - Legal CROWN CASTLE 2000 CORPORATE DRIVE CANONSBURG PA 15317 (724) 416-2442 holly.groschner@crowncastle.com Louie Rocha President CWA LOCAL 9423 2015 NAGLEE AVENUE SAN JOSE CA 95128 (408) 278-9423 louierocha@cwa9423.com Judy Pau DAVIS WRIGHT TREMAINE LLP 505 MONTGOMERY STREET, SUITE 800 SAN FRANCISCO CA 94111-6533 (415) 276-6587 judypau@dwt.com |
| Donald E. Hooper ES&C, INC. 116 STOCKTON AVENUE OCEAN GROVE NJ 07756 (732) 988-2685 hooperjd@verizon.net For: CCTA David Porte FASTBALL PARTNERS 87 DEPOT ROAD, SUITE 250 HARVARD MA 01451 (617) 512-4402 porte@fastballpartners.com W. Lee Biddle Attorney At Law FERRIS & BRITTON 401 WEST A STREET, SUITE 1600 SAN DIEGO CA 92101 (619) 233-3131 lbiddle@ferrisbritton.com C. Susie Berlin Attorney At Law MC CARTHY & BERLIN, LLP 100 PARK CENTER PLAZA, SUITE 501 SAN JOSE CA 95113 (408) 288-2080 sberlin@mccarthylaw.com For: NORTHERN CALIFORNIA POWER AGENCY Frances Yee PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, MC B8R SAN FRANCISCO CA 94105 (415) 973-6057 fsc2@pge.com Larry Nixon PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, MC B10A SAN FRANCISCO CA 94105 (415) 973-5450 lrn3@pge.com Law Department File Room PACIFIC GAS AND ELECTRIC COMPANY PO BOX 7442 SAN FRANCISCO CA 94120-7442 cpuccases@pge.com | Peter Van Mieghem Attorney At Law PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, ROOM 3107 SAN FRANCISCO CA 94105 (415) 973-2902 ppv1@pge.com Roxanne Piccillo PACIFIC GAS AND ELECTRIC COMPANY 77 BEALE STREET, B8R SAN FRANCISCO CA 94105 (415) 973-6593 rtp1@pge.com Judy Robb Consultant, Facilitator, Trainer ROBB GROUP 3539 MENDENHALL COURT PLEASANTON CA 94588 (925) 931-0965 robbgroup@earthlink.net For: ROBB GROUP David Dohren SAN DIEGO GAS & ELECTRIC COMPANY 8316 CENTURY PARK COURT, CP51D SAN DIEGO CA 92123 (858) 654-8777 ddohren@semprautilities.com For: SAN DIEGO GAS & ELECTRIC COMPANY Central Files SAN DIEGO GAS AND ELECTRIC COMPANY 8330 CENTURY PARK COURT, CP31E SAN DIEGO CA 92123 (858) 654-1240 centralfiles@semprautilities.com For: SEMPRA ENERGY UTILITIES Anthony Rabe SBC 3707 KINGS WAY, RM. C33A SACRAMENTO CA 95851 (916) 972-4173 ar2536@sbc.com For: SBC Mark Lyons SIMPSON PARTNERS LLP SUITE 1800 TWO EMBARCADERO CENTER SAN FRANCISCO CA 94111 (415) 732-1701 marklegal@sbcglobal.net |
| Case Administration SOUTHERN CALIFORNIA EDISON COMPANY 2244 WALNUT GROVE AVENUE ROSEMEAD CA 91770 case.admin@sce.com Richard Tom Attorney At Law SOUTHERN CALIFORNIA EDISON COMPANY 2244 WALNUT GROVE AVENUE ROSEMEAD CA 91770 (626) 302-4430 richard.tom@sce.com Jay Baumler Implementation Manager SPRINT PCS 18200 VON KARMAN, SUITE 100 IRVINE CA 92612 (949) 623-5997 Jay.M.Baumler@sprint.com For: Sprint PCS Marcel Hawiger Attorney At Law THE UTILITY REFORM NETWORK 711 VAN NESS AVENUE, SUITE 350 SAN FRANCISCO CA 94102 (415) 929-8876 marcel@turn.org Regina Costa THE UTILITY REFORM NETWORK 711 VAN NESS AVENUE, SUITE 350 SAN FRANCISCO CA 94102 (415) 929-8876 X312 rcosta@turn.org Margaret Tobias Attorney At Law TOBIAS LAW OFFICE 460 PENNSYLVANIA AVE SAN FRANCISCO CA 94107 (415) 641-7833 info@tobiaslo.com Brian Lafollette TURLOCK IRRIGATION DISTRICT PO BOX 949 333 EAST CANAL DRIVE TURLOCK CA 95381-0949 (209) 883-8396 bll@tid.org | Casey Hashimoto TURLOCK IRRIGATION DISTRICT 333 CANAL DRIVE TURLOCK CA 95380 (209) 883-8242 cjhashimoto@tid.org Michael Shames Attorney At Law UTILITY CONSUMERS' ACTION NETWORK 3100 FIFTH AVENUE, SUITE B SAN DIEGO CA 92103 (619) 696-6966 mshames@ucan.org Jacque Lopez Legal Assistant VERIZON CALIFORNIA INC CA501LB 112 LAKEVIEW CANYON ROAD THOUSAND OAKS CA 91362 (805) 372-6664 jacque.lopez@verizon.com Charles A. Johnson VERIZON CALIFORNIA INC. 201 FLYNN ROAD, MC CAM38NE2 CAMARILLO CA 93012 (805) 388-5077 chuck.johnson@verizon.com Lorraine A. Kocen VERIZON CALIFORNIA INC. 112 S. LAKEVIEW CANYON ROAD, CA501LS THOUSAND OAKS CA 91362-3831 (805) 372-6945 Lorraine.Kocen@verizon.com Michael Bagley VERIZON WIRELESS 15505 SAND CANYON AVENUE IRVINE CA 92612 (949) 286-8008 michael.bagley1@verizonwireless.com |

(END OF APPENDIX A)

As noted in the summary, sponsors of the settlement agreement are CPSD; IBEW; Communications Workers; PG&E; AT&T California; CCTA; Clearlinx Network Corporation; Crown Castle USA, Inc.; New Cingular Wireless PCS, LLC; NextG Networks of California Inc.; Omnipoint Communications, Inc., dba T-Mobile; Southern California Edison Company; Sprint Nextel; Verizon California Inc.; Verizon Wireless; and William Adams.  SDG&E, which owns its own poles, declined to join the Settlement.  It does not, however, oppose it.  Similarly, the California Municipal Utilities Association (CMUA) is not a signatory but does not oppose the settlement.

Verizon Wireless and Cingular Opening Comments, at 2 (capitalization altered).  Specifically, Verizon and Cingular argued that the Commission was precluded from adopting rules in the prior Proposed Decision for the following three reasons:  (1) Section 332(c) of the Communications Act expressly preempts RF-based rules; (2) FCC regulation regarding the health effects of RF emissions occupies the field, precluding any additional state regulation; and (3) even if the proposed rules were not expressly preempted by statute and the FCC had not occupied the field, adoption of the proposed rules would conflict with federal policy.  Id. at i.

Although the wireless carriers focused their preemption arguments on proposed signage and power-down requirements, Verizon Wireless and Cingular briefly noted that proposed clearance requirements also “appear[] to be based on concerns regarding RF exposure.”  Id. at 6, n.27 (citing exhibits that noted a potential connection between the clearances and RF exposure).  The decision we adopt today, however, makes it clear that Rule 94 vertical clearance requirements are based upon concerns regarding electric shock – not RF exposure.  Thus, the wireless carriers’ preemption arguments do not apply to the vertical clearance requirements adopted in this decision.

Another rule labeled Proposal 2A was offered by the California Municipal Utilities Association (CMUA) in its reply brief on March 28, 2006.  Proposal 2A was a composite of sections from Proposals 1 and 2.

Adams proposes one addition to Proposal 2, stating that if a disconnect device is installed, it “be protected from unauthorized operation by suitable means.”  (Adams Reply Brief, at 2.)

The provision suggested by intervenor Adams has been withdrawn.

ClearLinx Opening Brief, at 16.

Wireless Group Reply Brief, at 17.

CPSD, IBEW, PG&E, and SDG&E Reply Brief, at 25.

Transcript, at 3.

A supply conductor is one that carries electricity for the purpose of electric consumption, while a communication conductor carries electricity for the purpose of sending a communications signal.

SCADA antennas are Supervisory Control and Data Acquisition antennas that monitor the performance of electrical circuits.

In Comments on the Alternate Proposed Decision of Commissioner Brown, the Wireless Parties committed to abide by the terms of the settlement agreement with respect to any antenna placed on any jointly owned or used pole, whether or not the pole owner or other pole users are parties to the settlement.  (Id., at 3.)

Exhibit 1, Testimony of Raymond Fugere of CPSD, at 3 (Feb. 7, 2006).

Exhibit 10, Testimony of Marc Brock of PG&E, at 2 (Feb. 8, 2006).

Wireless Parties Comments on Alternate Proposed Decision of Commissioner Chong, at 2-3.

Wireless Parties Comments on Alternate Proposed Decision of Commissioner Brown, at 3.

Id., at 4.

ExteNet Reply Comments on Alternate Proposed Decision of Commissioner Chong.

Wireless Parties Comments on Alternate Proposed Decision of Commissioner Chong, at 4.

CCTA Reply Comments on Alternate Proposed Decision of Commissioner Chong.