[image: image1.png]Adelphia




[image: image19.wmf] 


[image: image20.png]@ 4,



[image: image21.wmf] 

[image: image22.wmf] 


[image: image23.png]veri-on



[image: image24.png](comcast.




[image: image25.jpg]7. Charter




July 2004
[image: image26.wmf] 

CPUC Headquarters
Sacramento Office
Los Angeles Office


505 Van Ness Avenue
515 “L” Street, Suite 1119
320 West 4th Street, Suite 500

San Francisco, CA 94102
Sacramento, CA 95814
Los Angeles, CA 90013

[image: image27.wmf] 



[image: image28.emf] 

Underground Distribution

PG&E

35%

SCE

51%

SDG&E

13%

Other

1%

Mountain

0%

Bear Valley

0%

Sierra Pacific

0%

PacifiCorp

1%

[image: image29.emf] 

UndergroundTransmission

PG&E

26%

SCE

60%

PacifiCorp

0%

Sierra Pacific

0%

Bear Valley

0%

Mountain

0%

Other

1%

SDG&E

14%


Page No.

Memorandum
1

I.     Introduction
2

A.  Purpose of Report
2

B.  CPUC’s Responsibilities
2

1.  General Order 95
2


2.   General Order 128
3

3.  General Order 165
3

4.  Incident Investigation & Customer Complaints
4

II.    Utility Companies Under the Jurisdiction of the CPUC
A.  Power Companies
5

1.  SCE
5
2.  PG&E
5
3.  SDG&E
5
4.  Other Investor Owned Companies
6
5.  Electric Cooperatives
6
6.  Municipalities
6
B.   Communication Companies
7
1.  SBC
7
2.  Verizon
7
3.  Others
7

C.   Cable Television
8

1.  Adelphia
8

2.  Charter Communications
8

3.  Comcast
8

4.  Cox Cable
8

III.   Annual Electric Report
9
A.  General Order 95 Inspections
9

1.  Utility Data
11

2.  USS Inspection Statistics
14

B.  General Order 128
15

1.  Utility Data
16

2.  USS Inspection Statistics
18

C.  General Order 165
19

Page No.

D.  Electric Incidents & Customer Complaints
20

1.
Overhead Equipment
22

2.  Underground Equipment
26

IV.   Additional Information
29

A.   Publications
29
1. How to Order
29

2. G.O. 95, 128, and 165
29

[image: image30.emf] 

0

5,000

10,000

15,000

20,000

25,000

30,000

35,000

40,000

Distribution Transmission

Distribution

24,287 35,800 8,916 508 160 52 15

Transmission

124 280 64 0 0 0.6 0

PG&E SCE SDG&E

PacifiCor

p

Sierra 

Pacific

Bear 

Valley

Mountain


[image: image31.wmf] 

[image: image32.wmf] 

Page No.

Table 1.
Summary of each Utility’s Overhead Equipment
11

Figure 1.
Miles of Overhead Transmission & Distribution Lines in California by Utility
11

Figure 2.
Percentage of Overhead Transmission Lines in California by Utility
12

Figure 3.
Percentage of Overhead Distribution Lines in California by Utility
12

Figure 4.
Percentage of poles in California by Utility
13

Figure 5.
Number of California Customers served by each Utility
13

Table 2.
Summary of the G.O. 95 Inspections Conducted
14

Table 3.
Tabulation of G.O. 95 Inspection Data
14

Table 4. 
Summary of G.O. 95 Violations Incurred by the Utility Companies
14

Table 5.
Summary of the Utility Company’s Underground Equipment
16

Figure 6. 
Miles of Underground Transmission & Distribution Lines in California


by Utility
16

Figure 7.
Percentage of Underground Transmission Lines in California by Utility
17

Figure 8.
Percentage of Underground Distribution Lines in California by Utility
17

Figure 9.
Percentage of Surface Mounted and Underground in California by Utility
17

Table 6.  
Summary of the G.O. 128 Inspections Conducted
18

Table 7.
Tabulation of G.O. 128 Inspection Data
18

Table 8.  
Summary of G.O. 128 Violations Incurred by the Utility Companies
18

Page No.
Table 9.  
Summary of Incident Investigations & Customer Complaints for USS
21
Table 10.
Tabulation of Incident Investigation Data
21

Table 11.
Summary of Leading Causes of Overhead Incidents reported to the CPUC


Relating G.O. 95
22

Figure 10.
Graph of the Leading Causes of Overhead Incidents reported to the CPUC


Relating G.O. 95
23

Figure 11. 
Percentage of Overhead Incidents Resulting in Fatalities
24

Figure 12. 
Percentage of Overhead Incidents Resulting in Injuries
24

Figure 13. 
Percentage of Overhead Incidents Resulting in Damage
25

Figure 14.
Percentage of Overhead Incidents Resulting in Media Attention
25

Table 12.
Summary of Leading Causes of Underground Incidents Relating to


G.O. 128
26

Figure 15.
Graph of Leading Causes of Underground Incidents Relating to


G.O. 128
26

Figure 16.
Percentage of Underground Incidents Resulting in Injuries
27

Figure 17.
Percentage of Underground Incidents Resulting in Damage
27

Figure 18.
Percentage of Underground Incidents Resulting in Media Attention
28

[image: image33.wmf] 


[image: image34.png]


[image: image35.wmf] 


This annual report of Electric Safety presents an account of various activities carried out under the California Public Utilities Commission’s (CPUC) electric safety program for the 2003 calendar year.

The CPUC has been entrusted with the safety jurisdiction over all electric and communication overhead and underground facilities in the state of California by Legislative mandate.  It is responsible for enforcing safety regulations, inspecting and investigating all work affected by the statutes, and making necessary additions and changes to regulations for promoting the safety of utility employees and the general public.  In addition, these standards promote improved reliability of electric service to the residents of California.  The electric safety program consists of the administration of General Orders (G.O.) 95, 128, 165, and Public Utilities Code, Sections 315, 768, 8026 through 8038, and 8051 through 8057. 

The State of California has the nation’s largest electric and communication system.  Therefore, it is important to maintain an adequate level of inspections and oversight to ensure that these systems are designed, constructed, operated, and maintained properly in accordance with the regulations for systems reliability and safety of the utility employees and the general public. The CPUC’s Utilities Safety Section (USS) implements the safety program by carrying out accident investigations, follow up investigations, compliance inspections, review of utilities’ reports and records, construction inspections, and special studies.  This is especially important with an aging system.

Acknowledgment

Jadwindar Singh, Utilities Engineer, under the general direction of Zee Wong, Chief of the Consumer Protection & Safety Division’s Safety & Reliability Branch, prepared this report.  We acknowledge the assistance provided by USS staff, the utilities, and other agencies in furnishing the data necessary for this report. 

[image: image36.wmf] 


[image: image37.wmf] 

[image: image38.png]‘Energy




A. PURPOSE OF REPORT


The purpose of this report is to document administration of General Order (G.O.) 95,

“Rules of Overhead Electric Line Construction”; G.O. 128, “Rules for Construction of Underground Electric Supply and Communication Systems”; and G.O. 165, “Inspection Cycles for Electric Distribution Facilities” for the calendar 2003 year as reported by utility companies and as accomplished by the USS staff.  It also provides general information on utility companies and statistical data on incidents and investigations related to electric facilities and other safety activities during 2003.

B. CPUC’s RESPONSIBILITIES
The CPUC is granted the authority to inspect, make further additions or changes as deemed necessary for the purpose of system reliability, safety to employees and the general public under the Public Utilities (PU) Code Section 8037.  Inspections and investigations are performed by USS staff to enforce G.O. 95, 128, and 165 regulations.  An overview of each general order is listed below.

1. General Order 95
G.O. 95, “Rules for Overhead Electric Line Construction”, became effective July 1, 1942.  Changes are noted in the order that reflect development of new materials and standards for line construction and changing operational practices.  The latest edition is dated 1998.

The purpose of these rules is to formulate, for the State of California, uniform requirements for overhead electrical line construction.  The application of these requirements will provide adequate service and secure safety to persons engaged in the construction, maintenance, operation or use of overhead electrical lines and to the general public.

The Commission also has the jurisdiction to regulate safety of cable and telephone corporations (PU Code Section 215.5 and 234).  Inspection of CATV and telephone facilities has been integrated with the field inspection program conducted on electric and telephone pole facilities.

2. General Order 128
G.O. 128, “Rules for Construction of Underground Electric Supply and Communications Systems”, became effective December 12, 1967.  The latest edition was issued in 1998.

The purpose of these rules is to formulate, for the State of California, uniform requirements for underground electrical supply and communication systems.  The application of these requirements will provide adequate service and secure safety to all persons engaged in the construction, maintenance, operation or use of underground electric systems (including telephone and cable), and to the general public.

3. General Order 165
G.O. 165, “Inspection Cycles for Electric Distribution Facilities”, became effective March 31, 1997 and it is the latest edition.

The purpose of this general order is to establish minimum inspection cycles requirements for electric distribution facilities addressing the utilities’ inspections (including maximum allowable inspection cycle lengths), condition rating, scheduling and performance of corrective action, record keeping, and reporting in order to ensure safe and high quality electrical service.  

G.O. 165 also implements the provisions of PU Code Section 364, which the California Legislature adopted when it enacted Assembly Bill 1890, Chapter 854, Statutes of 1996.

4. Incident Investigation & Customer Complaints 
In addition to enforcing the above general orders, USS staff conducts investigations of reportable incidents from the utility companies.  Section 315 of the Public Utilities Code provides that the Commission shall investigate the cause of accidents occurring upon the property of any utility.  

Reportable incidents, as updated in CPUC Decision (D.)98-07-097, Appendix B, are those which:  “(a) result in fatality or personal injury rising to the level of in-patient hospitalization and attributable or allegedly attributable to utility owned facilities; (b) are the subject of significant public attention or media coverage and are attributable or allegedly attributable to utility facilities; (c) involve or allegedly involve trees or other vegetation in the vicinity of power lines and result in fire and/or personal injury whether or not in-patient hospitalization is required.”  Incidents involving damage to property of the utility or others estimated to exceed $20,000 that are attributable or allegedly attributable to utility owned facilities are investigated as well.

The USS staff also handles all safety related customer complaints pertaining to G.O. 95, 128, and 165.  This may range from answering a telephone inquiry or correspondence, to conducting a formal investigation.  

[image: image39.wmf] 


[image: image40.wmf] 

[image: image41.wmf] 


The CPUC has been granted the authority by the Legislature to adopt and enforce G.O. 95, 128, and 165 requirements on investor owned utilities and municipalities.  There are a number of investor owned power and communication utility companies providing service in California as well as utilities operated by municipalities and cooperatives.   

A. POWER COMPANIES

1.  Southern California Edison Company
[image: image42.wmf] 


Edison International’s largest subsidiary is Southern California Edison Company (SCE).  SCE provides service to more than 4.6 million customers in a 50,000 square mile area.  SCE serves portions or all of California’s central and southern counties.

2.  Pacific Gas and Electric
[image: image43.wmf] 


Pacific Gas and Electric (PG&E) is one of the largest investor-owned companies in the U.S.  They provide electric service to about 5.2 million customers in California.  Their service area spans 70,000 square miles, including portions or all of 49 counties out of California’s 58 counties. 

3.  San Diego Gas and Electric

San Diego Gas and Electric (SDG&E) became a Sempra Energy company in 1998.  They provide electric service for 1.3 million customers in San Diego and portions of southern Orange County.  Their service area covers a total of 4,100 square miles in over 25 cities.

4.  Other Investor Owned Companies


 
         These companies also provide electric service to the people of California:

    ( Bear Valley Electric              
        ( Sierra Pacific Power Company

   ( Mountain Utilities (formerly     
       ( PacifiCorp

     Kirkwood Gas & Electric)
5.  Electric Cooperatives


  These electric co-operatives provide service to certain California customers:

 ( Surprise Valley Electrification Corp.   ( Anza Electric Cooperative

( Plumas-Sierra Rural Elect. Coop         ( Valley Electric Association, Inc.

6.  Municipalities


These California municipalities provide electric service to their customers.

       (   Alameda

     (   Anaheim

       (   Azusa

     (   Banning

       (   Biggs

     (   Burbank

(
Colton



         (   Glendale

(
Gridley



         (   Healdsburg

(
Imperial Irrigation District



         (   Lassen Municipal Utility District

· Lodi



         (   Lompoc

(
Los Angeles



         (   Modesto Irrigation District

(
Needles



         (   Northern Cal. Power Agency

(
Oroville-Wyandotte Irrigation District

         (   Palo Alto

(
Pasadena



         (   Redding

(
Riverside



         (   Roseville

(
Sacramento Municipal Utility District
  
         (   San Francisco

(
Santa Clara



         (   Shasta Lake

(
Southern Cal. Public Power Authority

         (   Tri-Dam Project

(
Trinity County



         (   Truckee Donner Public 







  Utility District

(
Turlock Irrigation District



         (   Ukiah

(
Vernon

B. COMMUNICATION COMPANIES

1. SBC (Southwestern Bell Telephone Co.)

SBC (previously Pacific Bell) has a total of 17.9 million access lines including residential, commercial, and others. The telephone service area covers approximately 51,000 square miles in California.

2. Verizon


In mid 2000, GTE formally changed their name to Verizon.  Verizon provides telecommunication services in the states of California, Nevada and Arizona. 

3.  Others


There are many smaller telephone companies in California under the jurisdiction of the CPUC.  These companies have overhead equipment that is inspected by the USS for compliance with G.O. 95.

C. CABLE TELEVISION

There are many cable television companies serving California cities.  They range from local companies serving one city to larger companies that may serve several cities.  A majority of the cable television companies are members of the California Cable Television Association (CCTA).  CCTA represents over 250 cable television systems that provide cable television service to over 6 million California homes.  The major cable television companies serving California are:

1.  Adelphia

[image: image44.wmf] 


2.  Charter Communications

3.  Comcast Corporation

Formerly AT&T Broadband, Comcast is the nation's largest cable company with 21.5 million subscribers.

4.  Cox Cable
    [image: image2.png]cox

COMMUNICATIONS







The USS is entrusted to enforce the provisions of General Orders 95, 128, and 165.  To do so, the USS conducts periodic inspection of both overhead and underground electric, communication and cable lines throughout the state.  This involves both field inspection and document audit.  Furthermore, the USS investigates accidents involving overhead and underground electric and communication lines as mandated by Public Utilities Code Section 315, to determine utilities’ compliance with the General Orders.  This section contains information and statistical data on the various electric related activities conducted by the USS during 2003.

A.    GENERAL ORDER 95 INSPECTIONS

In 2003, USS staff engineers conducted G.O. 95 field inspections of overhead lines   with utilities representatives’ participation.  The field inspections provide evidence on the quality of a utility's workmanship and maintenance programs.  Staff engineers inspect many miles of pole lines and document G.O. 95 violations found during the inspection.     

The field inspections are conducted over a three-day period.  The visual survey is conducted on the first day and the actual inspections are conducted on the remaining two days.  Typically, two staff engineers will use the first day of inspection to identify a specific area for the detailed inspections.  They will do this by conducting a visual survey of two communities/cities that appears to have numerous G.O. 95 violations.   The staff engineers will also contact the utility companies to request information such as circuit maps prior to conducting the visual survey.  

During the detailed field inspection, the staff engineers record the violations found on the overhead electric system, which includes poles, conductors, and all overhead equipment.  We request the power, communication, and cable utilities to participate in these inspections.  This expedites correction, as their personnel are also recording these violations.  

In 2003, USS personnel were divided into two units where each unit was assigned specific counties to conduct G.O. 95 inspections in California.  The following lists the counties each unit covered.

Northern Unit:  Alpine, Alameda, Amador, Butte, Calaveras, Colusa, Contra Costa, Del Norte, El Dorado, Glenn, Humboldt, Lake, Lassen, Marin, Mendocino, Mariposa, Merced, Modoc, Monterey, Napa, Nevada, Placer, Plumas, Sacramento, San Benito, San Francisco, San Joaquin, San Luis Obispo, San Mateo, Santa Clara, Santa Cruz, Shasta, Sierra, Siskiyou, Solano, Sonoma, Stanislaus, Sutter, Tehama, Trinity, Yolo, Yuba, plus portions of Fresno, Inyo, Kern, Kings, Madera, Mono, Santa Barbara, Tulare and Tuolumne that are served by Pacific Gas and Electric.

Southern Unit:  Imperial, Los Angeles, Orange, Riverside, San Diego, San Bernardino, Ventura, plus portions of Fresno, Inyo, Kern, Kings, Madera, Mono, Santa Barbara, Tulare and Tuolumne that are served by Southern California Edison and/or Los Angeles Department of Water and Power.

1.  Utility Data 

	Utilities
	Total Miles of Overhead Lines
	Transmission

Lines (miles)
	Distribution Lines (miles)
	Number

of Poles

	PG&E
	116,170
	18,488
	97,682
	2,274,980

	SCE
	72,800
	12,300
	60,500
	1,500,000

	SDG&E
	8,602
	1,741
	6,861
	232,163

	PacifiCorp
	3,061
	741
	2,320
	66,907

	Sierra Pacific
	1,128
	380
	748
	22,853

	Bear Valley
	202
	29
	173
	8,100

	Mountain
	0
	0
	0
	0

	Grand Total
	201,963
	33,679
	168,284
	4,105,003


Table 1.  Summary of each Utility’s Overhead Equipment.

[image: image3.wmf]0

10,000

20,000

30,000

40,000

50,000

60,000

70,000

80,000

90,000

100,000

Distribution

Transmission

Distribution

97,682

60,500

6,861

2,320

748

173

0

Transmission

18,488

12,300

1,741

741

380

29

0

PG&E

SCE

SDG&E

PacifiCorp

Sierra 

Pacific

Bear 

Valley

Mountain

Figure 1.  Miles of Overhead Transmission and Distribution Lines in California by Utility.

[image: image4.wmf]Overhead 

Transmission

Sierra Pacific

1%

Bear Valley

0%

PacifiCorp

2%

SDG&E

5%

Mountain

0%

PG&E

55%

SCE

37%


[image: image5.wmf]Overhead

Distribution

Sierra Pacific

0%

Bear Valley

0%

PacifiCorp

1%

SDG&E

4%

Mountain

0%

PG&E

59%

SCE

36%


[image: image6.wmf]Poles

SCE

37%

PG&E

54%

Mountain

0%

SDG&E

6%

PacifiCorp

2%

Bear Valley

0%

Sierra Pacific

1%


[image: image7.wmf]0

500,000

1,000,000

1,500,000

2,000,000

2,500,000

3,000,000

3,500,000

4,000,000

4,500,000

5,000,000

Customers Served

Residential

Commercial

Other

Residential

4,548,136

4,030,500

1,148,498

33,857

20,764

94

Commercial

481,665

481,500

137,781

7,277

1,504

554

Other

169,452

88,200

2,491

2,100

4

0

PG&E

SCE

SDG&E

PacifiCorp

Bear Valley

Mountain


Figure 5.  Number of California Customers served by each Utility.
2.  USS Inspection Statistics 

	For the 2003 Year 
	Total

	Number of Inspections 
	26

	Number of Inspection Days 
	79

	Number of Personnel Days
	144

	Number of Poles Inspected
	3383

	Total Number of Violations Cited  (See Table 4 for a summary.)
	6625


Table 2.  Summary of the G.O. 95 Inspections Conducted
	For the 2003 Year
	Figures

	Average Number of Inspection Days Per Week
	1.52

	Average Number of Personnel Days Per Inspection Week
	2.77

	Average Number of Violations Cited Per Inspection Day
	83.9

	Average Number of Poles Inspected Per Inspection Day
	42.82

	Average Number of Violations Per Pole
	1.96


Table 3.  Tabulation of G.O. 95 Inspection Data

	Utility Company
	Number of G.O. 95 Inspections
	Total G.O. 95 Violations
	Average Number of Violations   Per Inspection

	PG&E
	11
	649
	59

	SCE
	7
	496
	70.9

	SDG&E
	2
	63
	31.5

	Municipalities/Others
	6
	669
	111.5

	SBC
	21
	2045
	97.4

	Comcast
	11
	883
	80.3

	Adelphia
	8
	549
	68.6

	Verizon
	5
	547
	109.4

	Other Cable TV
	11
	724
	65.8


Table 4.  Summary of G.O. 95 Violations Incurred by the Utility Companies

B.    GENERAL ORDER 128 INSPECTIONS 


One staff engineer or inspector usually conducts General Order 128 underground facility inspections.  The inspection areas are selected similar to G.O. 95 inspections.  The staff engineer will also spend time reviewing the records required by G.O. 128 for an auditable and consistent program of inspection.  The inspection lasts three days and usually occurs in one utility operating district.  G.O. 128 inspections are conducted only with the electric utilities because communication utilities have fewer hazards associated with their facilities.  However, if the staff engineer finds any problems with the communication facilities, he will notify the communication company to correct the problems.

The G.O. 128 inspector joins a qualified utility lineman who opens the equipment enclosures containing live or energized equipment.  The live equipment may be contained inside an underground vault, a walk-in vault, or a subsurface enclosure such as a padmount.  The inspector records notes about the violations and prepares a formal report afterwards.  The report details the violations and directs the utilities to correct them.  The records are maintained similar to G.O. 95 inspections.

1.  Utility Data
	Utilities
	Total Miles of Underground Lines
	Transmission Lines (miles)
	Distribution Lines (miles)
	Surface Mounted

Structures
	Underground Structures

	PG&E
	24,411
	124
	24,287
	111,648
	285,084

	SCE
	36,080
	280
	35,800
	131,600
	207,970

	SDG&E
	8,980
	64
	8,916
	91,383
	41,776

	PacifiCorp
	508
	0
	508
	5087
	229

	Sierra Pacific
	160
	0
	160
	*
	*

	Bear Valley
	52.6
	0.6
	52
	600
	10

	Mountain
	15
	0
	15
	150
	24

	Grand Total
	70,207
	469
	69,738
	340,468
	535,093


Table 5.  Summary of the Utility Company’s Underground Equipment.  “*” Denotes statistic unavailable.


Figure 6.  Miles of Underground Transmission and Distribution Lines in California by Utility.





          


[image: image8.wmf]111,648

91,383

600

150

207,970

10

24

131,600

5087

285,084

41,776

229

0

50,000

100,000

150,000

200,000

250,000

300,000

PG&E

SCE

SDG&E

PacifiCorp

Bear Valley

Mountain

Surface Mounted

Underground


2.  USS Inspection Statistics
	For the 2003 Year
	Total

	Number of Inspections
	14

	Number of Inspection Days
	56

	Number of Personnel Days Used
	80

	Number of Structures Inspected
	739

	Number of Violations Cited (See Table 8 for a summary)
	571


Table 6.  Summary of the G.O. 128 Inspections Conducted

	For the 2003 Year
	Figures

	Average Number of Inspection Days Per Week
	1.08

	Average Number of Personnel Days Per Inspection Week
	1.54

	Average Number of Structures Inspected Per Inspection Day
	13.2

	Average Number of Violations Cited Per Inspection Day
	10.2

	Average Number of Violations Per Structure Inspected
	0.77


Table 7.  Tabulation of G.O. 128 Inspection Data

	Utility Company
	Number of       G.O. 128 Inspections
	Total G.O. 128 Violations
	Average Number of Violations   Per Inspection

	PG&E
	10
	226
	22.6

	SCE
	1
	90
	90

	SDG&E
	0
	-
	-

	Municipalities/Others
	3
	255
	85


Table 8.  Summary of G.O. 128 Violations Incurred by the Utility Companies

C.    GENERAL ORDER 165 INSPECTIONS 

General Order 165 became effective on March 31, 1997 for Pacific Gas & Electric, PacifiCorp, SDG&E, Sierra Pacific Power Company, and Southern California Edison. This General Order establishes minimum requirements for electric distribution facilities, regarding inspection (including maximum allowable inspection cycle lengths) scheduling and performance of corrective action, condition rating, record keeping, and reporting.  The requirements of this order are in addition to the requirements of G.O. 95 and G.O.128 to maintain a safe and reliable electric system.  These inspections are part of our regularly scheduled G.O. 95 and G.O. 128 inspections.

D.   ELECTRIC INCIDENTS & CUSTOMER COMPLAINTS

The USS staff receives and investigates reportable electric incidents from regulated utility companies.  Per Appendix B of D98-07-097, reportable incidents are those which (a) result in fatality or personal injury rising to the level of in-patient hospitalization and attributable or allegedly attributable to utility owned facilities; (b) are the subject of significant public attention or media coverage and are attributable or allegedly attributable to utility facilities, (c) involve or allegedly involve trees or other vegetation in the vicinity of power lines and result in fire and/or personal injury whether or not in-patient hospitalization is required.  Incidents involving damage to property of the utility or others estimated to exceed $20,000 that are attributable or allegedly attributable to utility owned facilities are investigated as well.

The electric utility companies are required to provide notice to the designated USS staff, via the USS Incident 1-800 number, within two hours of an incident.  The notice shall identify the time and date of the incident, the time and date of notice to the Commission, the location of the incident, casualties which resulted from the incident, identification of casualties and property damage, and the name and telephone number of a utility contact person.  

The designated USS staff is called the On-Call Engineer (OCE).  The OCE is responsible for receiving reportable incidents from the utility companies and he or she is available to do so 24 hours per day.   Each staff engineer assumes the OCE duties for an entire week several times per year.  The OCE or a staff engineer may investigate incidents at any hour, including weekends.  If it is determined that a G.O. violation was involved, staff prepares a report and recommends action against the utility.  

In addition, the USS maintains a database of outages and accidents to note trends.  If there is significant trending, the staff will investigate and work with utilities to correct the problem.  The database has been very useful in noting trends about a manufacturer defect, lack of tree trimming, or lack of preventive maintenance.  The Commission has initiated Order Instituting Investigations (OIIs) based on the results of USS’s investigations.  USS staff also handles customer complaints relating to G.O. 95 and 128 safety issues.  In addition to investigating incidents reported by the utility companies, USS investigates customer complaints involving alleged violations of the General Orders.   

	For the 2003 Year
	Total

	Number of Incidents Reported
	268

	Incidents Involving Overhead Equipment
	233

	Incidents Involving Underground Equipment
	35

	Number of Incidents Investigated
	268

	Number of USS Engineers** (not including management)
	18


Table 9.  Summary of Incident Investigations & Customer Complaints for the USS.

                ** Average taken since the number of engineers varied throughout the 2003 year.

	For the 2003 Year
	Figures

	Average Number of Incidents Reported Per Month
	22.33

	Percentage of Incidents Reported Involving Overhead Equipment 
	86.94%

	Percentage of Incidents Reported Involving Underground Equipment
	13.06%

	Average Number of Incidents Investigated Per Month
	22.33

	Percentage of Incidents Investigated Per Incidents Reported
	100%

	Average Number of Incidents Investigated Per USS Engineer
	14.88

	Average Number of Incidents Reported Per OCE Week
	5.15

	Average Number of OCE Weeks Per USS Engineer
	2.89


Table 10.  Tabulation of Incident Investigation Data.

1.  Overhead Equipment

The following table is a summary of leading causes of incidents in 2003 relating to overhead equipment:

	Electric Incident Causes
	Fatalities
	Injuries
	Damage
	Media Attention

	Aircraft
	1
	2
	1
	1

	Animal
	0
	0
	1
	2

	Booms/Cranes
	0
	1
	0
	2

	Fire 
	0
	0
	2
	3

	Insulator Failure 
	0
	0
	0
	1

	Irrigation Pipe
	0
	0
	0
	0

	Ladder
	1
	1
	0
	0

	Line Failure
	0
	0
	1
	6

	Metal Object
	0
	5
	0
	0

	Natural Cause
	0
	0
	1
	1

	Other Causes *
	1
	10
	3
	9

	Splice Failure
	0
	0
	1
	0

	Unknown
	0
	0
	2
	3

	Vegetation
	1
	6
	7
	2

	Vehicle
	0
	4
	3
	2

	Working Overhead
	2
	15
	0
	0

	Grand Total
	6
	44
	50
	34


Table 11.  Summary of Leading Causes of Overhead Incidents reported to the CPUC Relating G.O. 95.

Note:  Some incidents were reported under multiple criteria.  

* “Other Causes” includes events such trespassing, suicide, & vandalism.

[image: image9.wmf]0

2

4

6

8

10

12

14

Aircraft

Animal

Booms 

Crane

Falling Branch

Falling Tree

Fire 

Insulator Failure 

Irrigation Pipe

Ladder

Line Failure

Metal Object

Natural Cause

Other Causes

Splice Failure

Tree/Line Contact

Tree Trimmer

Unknown

Vehicle

Working Overhead

Fatalities

Injuries

Damage

Media Attention

Figure 10.  Graph of the Leading Causes of Overhead Incidents reported to the CPUC Relating G.O. 95.

[image: image10.wmf]Fatalities

Working 

Overhead

32%

Tree Trimmer

17%

Other Causes

17%

Ladder

17%

Aircraft

17%


Figure 11.  Percentage of Overhead Incidents Resulting in Fatalities.

[image: image11.wmf]Injuries

Tree Trimmer

7%

Vehicle

9%

Metal Object

11%

Falling Tree

2%

Ladder

2%

Falling Branch

5%

Booms 

2%

Aircraft

5%

Working 

Overhead

32%

Other Causes

25%


Figure 12.  Percentage of Overhead Incidents Resulting in Injuries.

[image: image12.wmf]Damage

Line Failure

5%

Natural Cause

5%

Other Causes

13%

Splice Failure

5%

Tree/Line Contact

22%

Tree Trimmer

5%

Unknown

9%

Vehicle

13%

Aircraft

5%

Animal

5%

Falling Branch

5%

Fire 

8%


Figure 13.  Percentage of Overhead Incidents Resulting in Damage.

[image: image13.wmf]Media Attention

Falling Branch

3%

Crane

6%

Animal

6%

Vehicle

6%

Insulator Failure 

3%

Line Failure

15%

Tree/Line Contact

3%

Natural Cause

3%

Other Causes

31%

Unknown

12%

Fire 

9%

Aircraft

3%


Figure 14.  Percentage of Overhead Incidents Resulting in Media Attention.

2.  Underground Equipment

The following table is a summary of leading causes of incidents in 2003 relating to underground equipment.

	Electric Incident Causes
	Fatalities
	Injuries
	Damage
	Media Attention

	Dig In
	0
	1
	9
	1

	Switch Malfunction
	0
	1
	1
	2

	Transformer Malfunction
	0
	2
	1
	4

	Underground Cable Failure
	0
	1
	0
	13

	Underground Splice Failure
	0
	0
	0
	2

	Working Underground
	0
	3
	1
	0

	Grand Total
	0
	8
	12
	20


Table 12.  Summary of Leading Causes of Underground Incidents Relating to G.O. 128.

[image: image14.wmf]0

2

4

6

8

10

12

Dig In

Switch

Malfunction

Transformer

Malfunction

Underground

Cable Failure

Underground

Splice Failure

Working

Underground

Fatalities

Injuries

Damage

Media Attention


Figure 15.  Graph of Leading Causes of Underground Incidents Relating to G.O. 128.

[image: image15.wmf]Injuries

Underground Cable 

Failure

13%

Dig In

13%

Working Underground

37%

Underground Splice 

Failure

0%

Switch Malfunction

13%

Transformer 

Malfunction

24%


Figure 16.  Percentage of Underground Incidents Resulting in Injuries.

[image: image16.wmf]Damage

Underground 

Cable Failure

0%

Dig In

76%

Working 

Underground

8%

Underground 

Splice Failure

0%

Switch 

Malfunction

8%

Transformer 

Malfunction

8%


Figure 17.  Percentage of Underground Incidents Resulting in Damage.

[image: image17.wmf]Media Attention

Underground 

Cable Failure

55%

Dig In

5%

Working 

Underground

0%

Underground 

Splice Failure

10%

Switch 

Malfunction

10%

Transformer 

Malfunction

20%


Figure 18.  Percentage of Underground Incidents Resulting in Media Attention.


A.   PUBLICATIONS
Copies of G.O. 95, 128, and 165 are available to the general public for purchase from the CPUC.

1.   How to Order 

2.   G.O. 95, 128, and 165 
G.O.  95:  
“Rules for Overhead Line Construction” book is available for purchase at 

  $20.00 each.

G.O. 128:  “Rules for Construction of Underground Electric Supply and Communication Systems” book is available for purchase at $5.00 each.

G.O. 165:  “Inspection Cycles for Electric Distribution Facilities”, the first copy of the G.O. leaflet is free with additional copies at $0.50 each.

   [image: image18.jpg]CPUC
ty
Branch










          Figure 3.


Percentage of Overhead Distribution Lines in California by Utility.





General Order 95 and 128 may be viewed at the CPUC web site.  The URL is:


http://www.cpuc.ca.gov/static/official+docs/i_go.htm








California Public Utilities Commission (most documents available)


320 West 4th Street, Suite 500


Los Angeles, CA 90013


(213) 576-7003





Documents, California Public Utilities Commission


505 Van Ness Avenue


San Francisco, CA 94102


(415) 703-1713








Call or Write


the CPUC at…








IV.   ADDITIONAL INFORMATION




















Figure 7.


Percentage of Underground Transmission Lines in California by Utility.








Figure 8.


Percentage of Underground Distribution Lines in California by Utility.








Figure 9.


Number of Surface Mounted and Underground Structures in California by Utility.  Note: Sierra Pacific’s statistics  unavailable.














         Figure 6B.


Percentage of Surface Mounted Each Utility Co. Has in California.














         Figure 6C.


Percentage of Underground Structures Each Utility Co. Has in California.

















          Figure 2.


Percentage of Overhead Transmission Lines in California by Utility.








           Figure 4.


Percentage of poles in California by Utility.











III.   aNNUAL ELECTRIC REPORT






































II.   UTILITY COMPANIES UNDER THE  


           JURISDICTION OF THE CPUC








I.   INTRODUCTION








MEMORANDUM








LIST OF TABLES AND FIGURES











Table of Contents














Promoting system reliability and safety for the general public.








Safety & Reliability Branch


Utilities Safety Section


2003 Electric Safety Report  











1
1

